|  | Seismic Hazard Study |  |
| --- | --- | --- |
|  | Prepared for Canada Nickel Co. |  |
|  | Prepared by SRK Consulting (Canada), Inc. and Paterson & Cooke AR-M2V4D 15/10/2026 |  |

|  | Seismic Hazard Study |  |
| --- | --- | --- |
|  | 15/10/2026 |  |
|  | Prepared for | Prepared by |
|  | Canada Nickel Co. | SRK Consulting (Canada), Inc. and Paterson & Cooke |
|  |  | Web: https://www.srk.com/ |
|  | Project No.: AR-M2V4D File Name: docx.en.docx |  |

Table of Contents

Signatures

Lead Author
Alejandro Verri Kozlowski
Principal Consultant, Practice Leader

Lead Author
Diana K. Reyes
Principal Consultant

SRK Consulting (Canada), Inc. and Paterson & Cooke

Printed: 15/10/2026

# 1	Executive Summary

SRK Consulting (Canada), Inc. and Paterson & Cooke prepared this report for Canada Nickel Co. under project AR-M2V4D, located in Timmins, Ontario, Canada. The study assessed the seismic hazard of the site Crawford and derived from that assessment the design earthquakes, the seismic design criteria for the tailings storage facilities and for conventional structures, and the dynamic properties and seismic coefficients of the slopes, together with the strong-motion records for the dynamic deformation analyses.

Probabilistic Seismic Hazard Assessment (PSHA). The probabilistic assessment quantifies the seismic hazard at each site as annual exceedance rates for specified ground-motion levels (Cornell, 1968; McGuire, 2004). It adopted the regional seismic source model CAN, with a logic tree comprising 6 branches, together with GMM logic trees for the active shallow crust (ASC), stable continental crust (SCC), subduction interface (SIF), SIS30, and SIS55 tectonic region types. The 10,000-year return period defines the Maximum Design Earthquake (MDE). Table 1.1 reports, for the site Crawford, the mean PGA by return period and site condition; on reference rock, VS30=760 m/s, the PGA of the MDE is 258 cm/s2.

Deterministic Seismic Hazard Assessment (DSHA). The deterministic assessment postulates, for each tectonic source capable of controlling the site demand, its maximum credible earthquake (MCE): the largest reasonably conceivable earthquake under the presently known tectonic framework (International Commission on Large Dams, 2016). The assessment postulated 2 scenarios with Mw from 4.5 to 6.5; the deterministic design spectrum MCE is their envelope. Table 1.1 reports, for the site Crawford, the PGA of the MCE and of the MCE (84%) by site condition; on reference rock, VS30=760 m/s, the PGA of the MCE is 232 cm/s2 and that of the MCE (84%) is 368 cm/s2.

Uncertainty Treatment. Epistemic uncertainty is represented through the logic trees of the source model and of the GMMs, and aleatory variability through the standard deviation of each ground-motion model; every spectrum is reported as its mean and its quantiles. Each deterministic scenario combines the equally weighted rupture variants, the GMM branches with their weights, and the record-to-record variability in a lognormal mixture. For the site Crawford, on reference rock, the 0.84 quantile of the PGA exceeds its mean by 39 % for the MDE and by 58 % for the MCE; Table 1.1 reports both statistics by site condition.

Site Response. The design ground motions are defined for the VS30 conditions evaluated at each site from the spectral demand at the surface. The design demands were evaluated for 7 site conditions, with VS30 from 180 to 1,500 m/s, by combining the direct logic-tree evaluation at each condition with the ST20 transformation of the demand at the reference condition of 760 m/s, conditioned on the PGA of the same realization. The mean PGA of the MDE is 265 to 308 cm/s2 across the site conditions. These results represent ergodic mean responses; a specific stratigraphic profile requires a separate site-response analysis. Table 1.1 reports, for each site and site condition, the probabilistic PGA together with the deterministic envelopes MCE and MCE (84%).

Seismic Record Selection. Ground-motion time histories provide the seismic input for the dynamic deformation analyses. A suite of 30 strong-motion records from 30 earthquakes and 5 databases was selected, with Mw 4.8 to 6.5 and epicentral distance Repi 1 to 263 km, and scaled by factors of 0.87 to 2.11 to the target spectrum defined for CFD at VS30 = 800 m/s. The suite-mean spectrum has a relative RMSE of 0.501 with respect to the target, and the ratio of the suite-mean PGA to the target PGA is 0.594. The delivered suite includes the time histories, intensity measures, spectra, and provenance metadata of the selected records.

Design Criteria for Tailings Storage Facilities. Seismic design for tailings storage facilities is based on a two-level performance framework: the Operating Basis Earthquake (OBE), associated with continued operation, and the Safety Evaluation Earthquake (SEE), associated with preventing a tailings release (International Commission on Large Dams, 2016; U.S. Army Corps of Engineers, 1995). The design earthquakes of the tailings storage facilities were evaluated under GISTM, CDA, and ANCOLD, for the consequence classes and the operation, closure, and post-closure lifecycle stages that each framework defines (Australian National Committee on Large Dams (ANCOLD), 2019; Canadian Dam Association (CDA), 2021; Global Tailings Review (ICMM, UNEP, PRI), 2020). On reference rock, the design PGA ranges from 8 to 361 cm/s2 across frameworks, consequence classes, and lifecycle stages. Table 1.2 reports, by consequence class and site condition, the design PGA of the GISTM framework at the operation stage; the design-criteria chapter reports the design PGA and design spectra by framework, consequence class, lifecycle stage, and site condition.

Design Criteria for Conventional Structures. Seismic design criteria for conventional structures were established from the hazard and site-response analyses in accordance with the site-specific procedure of ASCE/SEI 7-22, in which each MCER ordinate is the lesser of the risk-targeted probabilistic component and the code-prescribed deterministic component (Minimum Design Loads and Associated Criteria for Buildings and Other Structures, 2022). The MCER spectra and the design parameters were obtained for the 7 evaluated site conditions: SDS ranges from 0.09 to 0.14 g and SD1 from 0.02 to 0.05 g. Table 1.3 reports the design parameters by site and site condition.

Dynamic Properties of Slopes. The flexible sliding-block displacement models require the fundamental period of each potential sliding mass and the dynamic soil stiffness that determines it. The analyses considered 8 material scenarios over 5 slope geometries with heights between 27 and 135 m. The estimated fundamental period varies with the material class between 0.22 and 0.36 s in the lowest slope, and between 0.73 and 1.34 s in the highest one.

Newmark Permanent Displacements. The Newmark permanent displacement Dn quantifies the displacement induced by an earthquake and accumulated in the sliding mass and is the performance measure from which the seismic coefficients are derived. The Dn(ky) curves relate, for each combination of geometry, material, and design scenario, the yield acceleration ky to the expected permanent displacement; they were computed with the ensemble set of AM88, JB07, SR08, BT07, and BM19, with the reference magnitude assigned to each seismic demand and 300 realizations per demand and are read at the fractiles q=1−pe.

Performance-Based Seismic Coefficients. The horizontal pseudostatic coefficient kh is derived from the allowable permanent displacement Da of the potentially sliding mass (Bray & Travasarou, 2009; Macedo et al., 2018). The coefficients are reported at four relative displacement limits, Da/Hs = 0.1, 0.4, 1.0, 2.5%. Table 1.4 reports, for the MCE and the geometries analyzed, the range of the coefficient across the material scenarios at each limit, expressed as a percentage of the PGA.

The hazard curves, the probabilistic spectra, and the deterministic scenarios are presented in the Seismic Hazard Assessment annex. The selected records and their verifications are presented in the Seismic Record Selection annex. The design criteria and the structural design spectra are presented in the Seismic Design Criteria annex. The fundamental periods, the Newmark displacements, and the seismic coefficients are presented in the Ground-Motion Design Parameters annex.

Table 1.1: Peak ground acceleration by return period and site condition (siteID: CFD). Columns identified by VS30 (m/s) represent the site conditions. The TR rows (years) report the mean probabilistic PGA (cm/s2), and the MDE (84%) row reports the 0.84 quantile of the PGA for the return period of the MDE. The MCE and MCE (84%) rows report the deterministic envelope at its mean and 84th percentile, respectively, for the same site conditions.

| TR | 180 | 270 | 360 | 560 | 800 | 1250 | 1500 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 100 | 13 | 11 | 10 | 9 | 8 | 9 | 9 |
| 200 | 25 | 22 | 20 | 17 | 16 | 16 | 17 |
| 500 | 54 | 47 | 43 | 38 | 35 | 36 | 37 |
| 1,000 | 92 | 81 | 74 | 66 | 61 | 63 | 64 |
| 2,000 | 144 | 130 | 121 | 109 | 101 | 104 | 106 |
| 2,500 | 163 | 149 | 140 | 126 | 118 | 122 | 124 |
| 5,000 | 230 | 220 | 210 | 192 | 181 | 187 | 191 |
| 10,000 | 307 | 308 | 301 | 279 | 265 | 274 | 280 |
| MDE (84%) | 433 | 440 | 431 | 398 | 379 | 394 | 404 |
| MCE | 244 | 265 | 265 | 249 | 241 | 271 | 287 |
| MCE (84%) | 377 | 416 | 418 | 396 | 383 | 439 | 471 |

Table 1.2: Seismic design criteria of the GISTM standard at the Operation stage for CFD. Class is the consequence classification; TR is the governing annual-exceedance criterion expressed as a return period (yr) — where the standard sets the criterion between two return periods, the cell shows both and reports the average of their accelerations. Cells report the design PGA (cm/s2) that the criterion selects from the probabilistic hazard for VS30=180,270,360,560,800,1250,1500 m/s.

| Class | TR | 180 | 270 | 360 | 560 | 800 | 1250 | 1500 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Low | 200 | 25 | 22 | 20 | 17 | 16 | 16 | 17 |
| Significant | 1,000 | 92 | 81 | 74 | 66 | 61 | 63 | 64 |
| High | 2,500 | 163 | 149 | 140 | 126 | 118 | 122 | 124 |
| Very High | 5,000 | 230 | 220 | 210 | 192 | 181 | 187 | 191 |
| Extreme | 10,000 | 307 | 308 | 301 | 279 | 265 | 274 | 280 |

Table 1.3: ASCE/SEI 7-22 seismic design parameters obtained from the risk-targeted MCER spectrum. Each row identifies a site (siteID) and a site condition; VS30 is its shear-wave velocity, in m/s. SaM(0) is the MCER ordinate at zero period; SMS and SM1 are the MCER acceleration parameters; SDS and SD1 are the design acceleration parameters; these four ordinates and SaM(0) are in cm/s2. T0 and TS are the corner periods of the design spectrum, in seconds.

| siteID | VS30 | SaM(0) | SMS | SM1 | SDS | SD1 | T0 | TS |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| CFD | 180 | 141 | 209 | 80 | 139 | 54 | 0.077 | 0.385 |
| CFD | 270 | 133 | 206 | 68 | 137 | 45 | 0.066 | 0.328 |
| CFD | 360 | 126 | 198 | 57 | 132 | 38 | 0.057 | 0.286 |
| CFD | 560 | 115 | 175 | 40 | 117 | 27 | 0.046 | 0.229 |
| CFD | 800 | 107 | 154 | 32 | 103 | 21 | 0.042 | 0.208 |
| CFD | 1,250 | 111 | 133 | 30 | 89 | 20 | 0.046 | 0.228 |
| CFD | 1,500 | 113 | 130 | 30 | 87 | 20 | 0.046 | 0.229 |

Table 1.4: MCE seismic coefficients kh [% of PGA] from the ensemble model. Each cell reports the minimum–maximum range across the material scenarios, from their mean estimates. The range describes variation between materials; it is not a confidence interval or a simulation fractile. siteID identifies the site and Hs the slope height, in m. The remaining column headings are the relative displacement limits Da/Hs [%]. The column colors match the performance bands in the figures.

| siteID | Hs | 0.1% | 0.4% | 1% | 2.5% |
| --- | --- | --- | --- | --- | --- |
| CFD | 27 | 33.6–42.0 | 19.2–23.8 | 11.8–14.7 | 6.4–8.0 |
| CFD | 32 | 31.5–38.9 | 18.2–22.0 | 11.4–13.4 | 6.3–7.4 |
| CFD | 35 | 30.6–38.1 | 17.4–21.2 | 10.6–12.9 | 5.8–6.9 |
| CFD | 50 | 25.7–29.5 | 14.0–16.2 | 8.1–9.6 | 4.2–5.1 |
| CFD | 135 | 16.3–17.5 | 7.7–8.4 | 4.1–4.5 | 2.2–2.4 |

# 2	Introduction

## 2.1	Objectives

The primary objectives of this study are as follows:

Seismic Hazard: Quantify annual exceedance probabilities for ground-motion intensity measures at the site using probabilistic seismic hazard analysis. Compute site-specific hazard curves and uniform hazard spectra at reference-rock conditions. Perform hazard deaggregation to identify controlling magnitude, distance, and epsilon (normalized residual) scenarios at each governing hazard level. Summarize the hazard results as mean and fractile annual-exceedance-probability curves for defined site conditions.

Site Response: Compute site-specific peak ground acceleration and spectral ordinates through two ergodic estimates — the direct evaluation of the ground-motion model tree, with each model’s own site terms, at each evaluated condition, and the transformation of the reference-rock motion through the Stewart and Hashash (2020) NGA-East ergodic amplification model — and combine their probability distributions as a finite mixture to define the design demand. Present the results as tables and figures summarizing peak ground acceleration and uniform hazard spectra for all evaluated site conditions and fractiles.

Slope Design: Quantify permanent slope displacements and derive performance-based horizontal seismic coefficients (kmax, kh) for slope stability design. Displacements are estimated using a weighted ensemble of rigid- and flexible-block Newmark models across all geometry classes, material scenarios, MDE and MCE demand scenarios, and allowable displacement thresholds. Seismic coefficients are determined by inversion of the displacement framework for each prescribed performance objective. Summarize the kmax and kh design values for all geometry–material–demand-scenario combinations.

Design Criteria: Establish seismic design criteria for tailings storage facilities based on international standards and consequence classification. Assign design earthquakes and performance objectives for all project lifecycle phases, including operation, closure, and post-closure, as required by GISTM, CDA, and ANCOLD. Determine Maximum Credible Earthquake (MCE) scenarios in accordance with regulatory requirements. Define the probabilistic design spectra and the associated ground motions for each operational stage and consequence rating. Establish, for conventional structures, the MCER spectra of the ASCE/SEI 7-22 (IBC 2024) site-specific procedure — the risk-targeted Maximum Considered Earthquake — and derive from them the design spectra, defined as two-thirds of the MCER ordinates, with their SDS and SD1 parameters.

Seismic Record Selection: Select, through magnitude and distance windows tied to the scenarios that control the hazard and with at most one record per event, a set of strong-motion records that represents the amplitude, duration, and frequency content of the seismic demand; process each horizontal component by removing the low-frequency mode associated with drift and noise and normalizing the energy of the reconstructed signal; scale the set to reproduce the mean of the site-specific target spectrum and to contain the individual spectra within its envelopes; and verify the resulting compatibility through the error of the spectral mean, the PGA ratio, and the contained fraction of ordinates, preserving the identification of events, stations, and intensity measures for the dynamic deformation analyses.

Uncertainty Modeling: Propagate epistemic uncertainty through logic-tree branching and aleatory variability through probabilistic integration across all analysis components. Propagate the hazard and model uncertainties in site response through analytical integration of the distributions to generate fractile site-response spectra. Aggregate uncertainties in ground-motion intensity measures, site response, and displacement models to generate fractile bands for Newmark displacements and performance-based seismic coefficients.

## 2.2	Format

This report presents the seismic hazard assessment and the seismic design criteria of the project. This document is delivered in printable format (DOCX/PDF) as a companion reference and includes the principal seismic design parameter tables. Dynamic charts and interactive maps are available only in the HTML version. The HTML version is the complete and official report, available online and for local consultation. The seismic hazard assessment is documented in the Seismic Hazard Assessment annex. The seismic design criteria are presented in the Seismic Design Criteria annex. The ground-motion design parameters are presented in the Ground-Motion Design Parameters annex. Seismic record selection and processing are documented in the Seismic Record Selection annex.

## 2.3	Disclaimer

The opinions expressed in this Report have been based on the information supplied to SRK Consulting (Canada), Inc. and Paterson & Cooke (SRK-PC ) by Canada Nickel Co. (CN). The opinions in this Report are provided in response to a specific request from CN to do so. SRK-PC has exercised all due care in reviewing the supplied information. Whilst SRK-PC has compared key supplied data with expected values, the accuracy of the results and conclusions from the review are entirely reliant on the accuracy and completeness of the supplied data. SRK-PC does not accept responsibility for any errors or omissions in the supplied information and does not accept any consequential liability arising from commercial decisions or actions resulting from them. Opinions presented in this report apply to the site conditions and features as they existed at the time of SRK-PC’s investigations, and those reasonably foreseeable. These opinions do not necessarily apply to conditions and features that may arise after the date of this Report, about which SRK-PC had no prior knowledge nor had the opportunity to evaluate.

# 3	Seismic Hazard Assessment

## 3.1	Probabilistic Seismic Hazard Assessment (PSHA)

Probabilistic seismic hazard analysis (PSHA) quantifies the rate at which different levels of ground motion may be exceeded at the site. The assessment represents the range of magnitudes, locations, and ground motions through the seismic-source model and the ground-motion prediction models, and applies the total-probability theorem over the scenarios that can contribute to the demand (Cornell, 1968; McGuire, 2004).

The assessment adopted the regional source model CAN, with a logic tree comprising 6 branches, together with GMM trees for the ASC, SCC, SIF, SIS30, SIS55 regimes. The calculation domain begins at Mw 4.5, considers sources up to 1,000 km, and truncates the residual distribution of the GMMs at ±3.0σ.

Each seismic source contributes to the exceedance rate through its occurrence rate and through the magnitude and distance distributions of its earthquakes. For a seismic source s, ν0(s) is its annual occurrence rate above the minimum magnitude Mmin, m is the moment magnitude, and r gathers the source-to-site distance metrics required by the GMMs. The domain D comprises the admissible rupture locations and geometries for the source. The probability density functions (PDF) fM,s(m) and fR∣M,s(r∣m) describe the normalized magnitude and distance distributions of the earthquakes within source s, Mmax(s) is the upper magnitude bound of the source, I is the intensity measure, and i* the level whose exceedance is evaluated. With these definitions, the contribution of the source is

λI(i*)(s) = ν0(s)MminMmax(s)D​PI>i* | m,r fM,s(m) fR∣M,s(r∣m) dr dm	(3.1)

This formulation is a direct application of the total-probability theorem in continuous form, integrating over all magnitudes and locations of earthquakes from source (s) that could contribute to exceedance of level i*. Aleatory variability represented in the recurrence, magnitude, location, and ground-motion models is propagated through the integration (Baker et al., 2021; McGuire, 2004).

The total hazard at the site sums the contributions of all the sources considered: if multiple seismic sources contribute to the hazard at the site, the total annual exceedance rate λI(i*) is obtained by summing the contributions from all sources,

λI(i*) = s=1NSλI(i*)(s)	(3.2)

Expression 3.2 assumes NS independent sources, each with its own occurrence rate and distributions, and evaluates λI(i*)(s) for each source through the hazard integral. This linear superposition is valid under the assumption that earthquake occurrences in different sources are independent, typically modeled as independent Poisson processes. The result is a seismic-hazard curve that quantifies the rate at which various ground-motion levels are exceeded at the site.

The term P[I>i*∣m,r] of the integral is supplied by the ground-motion model (Chapter 3.3), which enters PSHA through its median ηI and its total standard deviation σlnI. Variations among competing GMPEs in either quantity modify the exceedance rates, particularly at long return periods, where the integral weights the upper tail of the lognormal distribution (GEM Foundation, 2023).

The hazard curve is expressed as an annual rate, as a probability of exceedance over an exposure interval, and as a return period. The annual exceedance frequency λI(i*) obtained from the hazard integral 3.1 is the mean number of exceedances per year of level i*, and the curves labelled AEP in this report present that rate, in 1/year. If exceedances follow a Poisson process in time, the exact probability of at least one exceedance during a single year is

P1yr[I>i*]=1−exp[−λI(i*)]	(3.3)

For small rates, P1yr≈λI, because e−λ≈1−λ. By extension, the probability of exceedance in T years is PT(I>i*)=1−exp[−λI(i*)T] under stationarity; this relation converts the mean annual rate into the probability for the exposure interval. The return period TR, or mean return interval, is expressed in years, does not represent a deterministic recurrence time, and is defined by

TR=1λI(i*).	(3.4)

The hazard integral propagates the aleatory variability of its models; the epistemic uncertainty of the models themselves is represented through the logic trees of the regional source model (Section 3.2.4) and of the GMMs (Chapter 3.3). Each branch specifies an alternative characterization with a non-negative weight, and the weights of each set sum to one. The recurrence, geometry, and maximum-magnitude parameters of each source enter the integral through the magnitude and distance densities. The GMM trees represent the active tectonic regimes separately and weight their prediction models; record-to-record aleatory variability remains in the standard deviation of each GMM. OpenQuake evaluates the hazard integral for the tree realizations and forms the requested statistics by weighting the resulting curves (Global Earthquake Model Foundation, 2024).

In this assessment, the assessment adopted the CAN model, whose logic tree comprises 6 branches; the GMM trees comprise ASC (4 branches), SCC (16 branches), SIF (4 branches), SIS30 (4 branches). The probabilistic output at reference rock (VS30=760 m/s) reports the mean and the 0.05, 0.1, 0.16, 0.5, 0.84, 0.9, 0.95 quantiles.

The PSHA aggregates the contributions of all plausible earthquake scenarios in the total exceedance rate, obscuring the specific combinations of magnitude (M), source-to-site distance (R), and ground-motion residual (ε) that control site hazard. Hazard disaggregation quantifies the relative contribution of each scenario class, binned by magnitude mk, distance rj, and residual εℓ, to the annual frequency of exceedance at a specified ground-motion threshold i* (Bazzurro & Cornell, 1999).

Disaggregation is performed at a target hazard level, defined by an annual exceedance probability or return period. This produces conditional probability distributions over scenario bins and identifies controlling scenario parameters responsible for site hazard (Kramer, 1997). The joint exceedance rate for scenario (mk,rj,εℓ) from source s is

ΔλI(i*,mk,rj,ε)(s)=1{ε≥ε*(mk,rj)} φ(ε) fM,s(mk) fR∣M,s(rj∣mk) ν0(s),	(3.5)

where φ is the standard normal probability density function and 1⋅ is the indicator function; the ground-motion exceedance probability and the total annual exceedance rate that enter the formulation are those defined in the hazard analysis (see 3.1, 3.13). Integration over ε yields the two-dimensional (M-R) formulation. Partitioning parameter space into magnitude bins mk, distance bins rj, and residual bins εℓ, the contribution from bin (k,j,ℓ) is

λk,j,ℓ(i*)=s=1NSmk​rj​εℓ​ΔλI(i*,mk,rj,ε)(s)dε dr dm	(3.6)

Hazard disaggregation applies Bayes’ theorem to the joint distribution of scenario parameters and ground-motion exceedance: the conditional probability that exceedance of i* is produced by this bin is

P[M=mk,R=rj,ε=εℓ∣I>i*]=θk,j,ℓ=λk,j,ℓ(i*)λI(i*)	(3.7)

and the marginal probabilities are obtained by double summation over the other indices, over distance and residual for the magnitude,

PM∈mk∣I>i*=j​ℓ​θk,j,ℓ	(3.8)

over magnitude and residual for the distance,

PR∈rj∣I>i*=k​ℓ​θk,j,ℓ	(3.9)

and over magnitude and distance for the residual, whose marginal distribution quantifies the contribution of ground-motion residual bins to the exceedance:

Pε∈εℓ∣I>i*=k​j​θk,j,ℓ	(3.10)

The modal scenario is the (k,j,ℓ) bin for which θk,j,ℓ of 3.7 attains its maximum. The mean scenario is the average magnitude–distance pair of the conditional distribution, weighted by those contributions.

In this report, the OpenQuake disaggregation outputs are presented as magnitude-distance (Mag_Dist) matrices. The calculation uses magnitude bins of 0.1 Mw, distance bins of 10 km, and the intensity measures PGA, Sa(0.10 s), Sa(0.20 s), Sa(0.50 s), and Sa(1.00 s). The reported heatmaps and modal table therefore summarize the two-dimensional M-R contribution surface for each selected return period and oscillator period. Disaggregation provides a data-driven basis for scenario selection in engineering analysis. The modal scenario and the highest-probability bins identified through disaggregation correspond to the earthquake characteristics most responsible for exceedance at the design ground-motion level.

### 3.1.1	Hazard Curves and Spectra

AEP curves report the mean annual exceedance rate, λI, in 1/year for each ground-motion threshold. Total hazard curves integrate the contribution of all sources considered, and by-source curves retain the individual contribution. The exact probability for an exposure interval is presented in the PoE curves.

Probability of exceedance (PoE) curves report the probability that a specified ground-motion intensity is exceeded over the project exposure interval; under the Poisson process, that probability is converted from the mean annual exceedance rate of the AEP curves. The magnitude-distance disaggregation of each site, summarized by return period and oscillator period, closes the probabilistic assessment.

Table 3.1: Seismic hazard deaggregation summary for site CFD. Each row corresponds to a return period TR, in years, and each column group to an oscillator period Tn, in seconds, with Tn=0 corresponding to PGA. Within each group, Mw is the moment magnitude of the magnitude–distance block contributing most to exceedance, dimensionless, and R is the source-to-site distance of that same block, in km; both are the coordinates of the block centre on the same block grid used by the deaggregation figures.

| TR | Tn=0 |  | 0.1 |  | 0.2 |  | 0.5 |  | 1 |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| TR | Mw | R | Mw | R | Mw | R | Mw | R | Mw | R |
| 100 | 5.25 | 62 | 5.25 | 262 | 5.25 | 62 | 6.25 | 838 | 6.25 | 838 |
| 200 | 5.25 | 62 | 5.25 | 62 | 5.25 | 62 | 5.25 | 38 | 6.75 | 838 |
| 500 | 5.25 | 38 | 5.25 | 62 | 5.25 | 38 | 5.25 | 38 | 6.75 | 812 |
| 1,000 | 5.25 | 38 | 5.25 | 38 | 5.25 | 38 | 5.25 | 38 | 6.75 | 712 |
| 2,000 | 5.25 | 12 | 5.25 | 38 | 5.25 | 12 | 5.25 | 12 | 6.75 | 288 |
| 2,500 | 5.25 | 12 | 5.25 | 38 | 5.25 | 12 | 5.25 | 12 | 6.75 | 288 |
| 5,000 | 5.25 | 12 | 5.25 | 12 | 5.25 | 12 | 5.25 | 12 | 6.75 | 262 |
| 10,000 | 5.25 | 12 | 5.25 | 12 | 5.25 | 12 | 5.25 | 12 | 5.75 | 12 |

The hazard curves and probabilistic spectra are developed in the Seismic Hazard Assessment annex.

## 3.2	Seismic Source Characterization

### 3.2.1	Seismotectonic Setting

### 3.2.2	Seismicity

### 3.2.3	Neotectonics

### 3.2.4	Regional Sources (SSM)

## 3.3	Ground Motion Models (GMM)

The term P[I>i*∣m,r] in the hazard integral 3.1 represents the ground-motion model’s probabilistic prediction of exceedance and is obtained from ground-motion prediction equations (GMPEs). GMPEs are empirical or semi-empirical models that predict the statistical distribution of ground-motion intensity measures, such as PGA and spectral acceleration, given an earthquake’s characteristics. A GMPE typically provides a median predicted ground motion, often in log10 or natural-log units, as a function of parameters such as magnitude M, source-to-site distance R, and site condition, along with an estimate of aleatory variability, the standard deviation σ of the logarithmic residuals (Boore & Atkinson, 2008). A generic form of a GMPE for an arbitrary intensity measure I is given in 3.11, where F and S are indicator variables for fault type, such as reverse or normal, and site class, such as rock or soil, and ε is a standard-normal (zero-mean) random variable representing the random scatter, with σlnI being the log-standard deviation (Boore & Atkinson, 2008):

lnI≈ηI(m,r,F,S) + ε σlnI,	(3.11)

If ηI(m,r,F,S) denotes the median intensity I (in linear units) for magnitude m at distance r and σlnI is the standard deviation of lnI, then the conditional exceedance probability is

P[I>i*∣m,r] = 1 − Φε*,	(3.12)

where Φ is the standard-normal cumulative-distribution function and ε*, the number of standard deviations by which i* exceeds the median prediction for scenario (m,r,F,S), is

ε* = lni*−lnηI(m,r,F,S)σlnI	(3.13)

The total aleatory standard deviation σlnI satisfies the quadrature relation

σlnI2=τ2+ϕ2	(3.14)

where τ is the between-event (inter-event) standard deviation and ϕ is the within-event (intra-event) standard deviation, both expressed in natural-log units. Under the mixed-effects decomposition adopted by most modern empirical GMPEs, the total residual for record j belonging to event i is partitioned as

εij=ηi+δij	(3.15)

where ηi∼N(0,τ2) is the between-event residual for event i, representing systematic source-to-source variation not captured by the median functional form, and δij∼N(0,ϕ2) is the within-event residual for record j, representing path and site variability not resolved by the median prediction; the two residual components are assumed mutually independent. All three quantities σlnI, τ, and ϕ are period-dependent in most modern GMPEs and are tabulated or parameterized as part of the published model; non-ergodic formulations further partition τ and ϕ into site-specific and path-specific components, and the models of the adopted trees, documented in the Ground Motion Prediction Models appendix, are predominantly ergodic.

The predictor variables entering a GMPE vary by model and tectonic region type, but the following notation applies consistently across all models of the adopted trees. Moment magnitude Mw is the primary source-size parameter. Each model declares the distance metric it requires as part of its implementation. Site amplification is parameterized primarily by VS30, the time-averaged shear-wave velocity in the uppermost 30 m. Basin depth is captured by z1.0, the depth to the horizon where shear-wave velocity first reaches 1.0 km/s, and by z2.5, the depth to the 2.5 km/s horizon. Rupture geometry descriptors include ztor, the depth to the top of the rupture plane; the fault dip angle; the rake angle characterizing faulting style; the along-dip rupture width W; and hypocentral depth h. For subduction models, a binary backarc flag distinguishing forearc and backarc site positions is additionally required by certain implementations.

The ground-motion characterization adopts an independent logic tree for each tectonic region type present in the source model. The Ground Motion Prediction Models appendix documents, regime by regime, the branches that compose each tree – each one a ground-motion prediction equation (GMPE) with its weight – and the calibration context of each model.

GMMs are among the main contributors to the epistemic uncertainty of the PSHA, together with source-model components such as fault geometry, seismicity rates, and magnitude-frequency distributions. Unlike aleatory variability, epistemic uncertainty represents incomplete scientific knowledge of the true ground-motion process: it is in principle reducible with additional data and is represented through a discrete set of alternative models. In regions with scarce strong-motion records, the medians of candidate GMPEs can diverge substantially over the spectral periods and magnitude-distance ranges of engineering interest, and that dispersion is frequently the main contributor to the uncertainty band of the hazard curve at low exceedance rates; model uncertainty is therefore represented explicitly through a logic tree that samples the space of possible alternatives.

Each logic tree is defined for one tectonic region type and comprises a single branching level. Each branch specifies an alternative GMPE with a non-negative weight wk satisfying the normalization condition

k=1Nwk=1,  wk≥0	(3.16)

where N is the number of branches in the set. The weights define a discrete probability distribution over the candidate GMPEs; when all models receive equal weight, wk=1/N, the tree represents a state of maximum model uncertainty, with no prior preference for any formulation. The tree is propagated by evaluating the hazard integral separately for each branch and combining the resulting curves with their weights (GEM Foundation, 2023), so that the mean hazard curve is the weighted average

λI(i*)=k=1Nwk λI(k)(i*)	(3.17)

where λI(k)(i*) is the annual exceedance rate calculated with the GMPE of branch k. The full distribution over branches also allows fractile hazard curves at prescribed probability levels, which characterize the dispersion originated by the GMM epistemic uncertainty.

The trees of this assessment assign equal weights to their branches, as their appendix sections detail. This weighting is a grounded epistemic response: where the strong-motion records are insufficient to discriminate statistically among candidate formulations, there is no empirical basis for assigning systematically greater weights to one model family, and differential weights would introduce an apparent precision without support, at the risk of under-representing the true range of epistemic uncertainty. From information theory, the uniform distribution is the maximum-entropy assignment under a state of equal prior knowledge (Motaghed et al., 2023).

The complement of that weighting is the breadth of the ensemble. A large set of diverse genealogies – European, New Zealand, Taiwanese, and global NGA-West2 calibrations in active crust; eastern North America and the European and Australian cratons in stable crust; regional databases from Chile, Japan, Taiwan, and Mexico together with the global NGA-Subduction compilation in the subduction regimes – spans the widest defensible range of predictions and reduces the risk that the mean curve be dominated by a narrow group of models sharing common assumptions or training data (U.S. Nuclear Regulatory Commission, 2012).

Comparisons among GMMs require an operation distinct from the combination of hazard curves. For a fixed cell x=(Mw,Repi,h,Tn,VS30), each branch k contributes a lognormal distribution with logarithmic median μk(x) and total logarithmic standard deviation σk(x). The cumulative distribution function of the weighted mixture is

FSa(a∣x)=k=1Nwk Φ​lna−μk(x)σk(x).	(3.18)

and the tabulated quantiles are obtained by numerically inverting this function for the seven probability levels p of the products, 0.05, 0.10, 0.16, 0.50, 0.84, 0.90, and 0.95,

Sa(p)(x)=FSa−1(p∣x).	(3.19)

while the arithmetic mean of the mixture is evaluated directly from its lognormal components:

E[Sa∣x]=k=1Nwkexp​μk(x)+σk2(x)2.	(3.20)

The separation among the branch medians represents the epistemic dispersion across models, and each σk retains the aleatory variability of its formulation; the p5–p95 band is bounded by the 5th and 95th percentiles of the mixed conditional distribution and gathers both contributions. This per-cell mixture is used in the attenuation curves, the comparative spectra, and the conditional scenario evaluations. In the PSHA, each branch is integrated separately before the hazard curves are weighted; the resulting uniform hazard spectra constitute the spectral input of the probabilistic estimation of Newmark displacements (Chapter 5.2), so the influence of the GMMs reaches that stage through those spectra (Verri Kozlowski, 2026a).

The seismic hazard assessment is documented in the Seismic Hazard Assessment annex.

## 3.4	Deterministic Seismic Hazard Assessment (DSHA)

The deterministic assessment characterizes the seismic demand through a finite set of postulated rupture scenarios. Each scenario represents the maximum credible earthquake (MCE) of one source: the largest earthquake reasonably conceivable along a recognized fault or within a geographically defined tectonic province, under the presently known tectonic framework (International Commission on Large Dams, 2016). Each scenario preserves the identity of the tectonic source, its tectonic regime, the adopted moment magnitude, the rupture geometry, and the source-to-site distances required by the ground-motion models. The objective is to obtain the conditional distribution of spectral acceleration for each scenario and to construct, period by period, the deterministic envelopes used in the comparison with the probabilistic hazard.

The construction of the scenarios starts from the tectonic characterization adopted for each source: tectonic regime, magnitude, and explicit geometric rupture variants. Each realization represents one of those variants, receives the same weight, and supplies the distance vector required by the ground-motion models. The logic tree corresponding to the tectonic regime (Chapter 3.3) supplies the model branches and their weights; each combination of rupture realization and GMM branch constitutes a component of the scenario distribution (GEM Foundation, 2023).

The two assessments differ in the treatment of the conditional exceedance probability: the probabilistic assessment integrates it over the recurrence of the sources, whereas the deterministic assessment computes that same probability conditioned on the occurrence of the postulated scenario. For the scenario e=(me,re,θe), me is the moment magnitude, re collects the source-to-site distances, and θe contains the remaining rupture parameters and the site condition. The intensity I represents the maximum horizontal ordinate Sa(Tn) at period Tn, and i* is the level whose exceedance is evaluated. Each component of the scenario distribution is a lognormal prediction. For a rupture realization r and a GMM branch g, the logarithm of the intensity is represented by a normal distribution with mean μrg=lnηI(me,rr,F,S), evaluated with the corresponding formulation, and standard deviation σrg=σlnI. In this expression, ηI is the median intensity in linear units, rr is the distance vector of the realization, F represents the faulting style, and S the site condition. Identifying each pair (r,g) by k, the component weight is

wk=vgNR,  k​wk=1,	(3.21)

where vg is the weight of branch g of the logic tree and NR is the number of explicit rupture variants, represented by equally weighted realizations. With those weights, the conditional exceedance probability of the scenario is obtained as

P​I>i*∣e=k​wk1−Φ​lni*−μkσk,	(3.22)

where μk and σk correspond to component k and Φ is the standard normal cumulative distribution function, and the conditional cumulative distribution function of the intensity is the complement of the exceedance:

G(a∣e)=k​wk Φ​lna−μkσk.	(3.23)

The fractiles are obtained by numerical inversion of G(⋅∣e),

Q(p∣e)=inf{a:G(a∣e)≥p}.	(3.24)

and the mean is computed directly from the lognormal components:

E[Sa∣e]=k​wkexp​μk+12σk2.	(3.25)

The calculation obtains seven fractiles and the mean for each scenario, and the evaluation is carried out analytically from (μk,σk,wk); the comparison in this chapter presents the mean of each scenario and retains the 84th percentile only in the MCE (84%) envelope. The ordinates correspond to the maximum horizontal component at 5% of critical damping and are evaluated at the reference condition Vref=760 m/s; the PGA corresponds to Tn=0. This condition provides the computational reference from which the site-response model derives the site conditions actually evaluated (Chapter 4.1).

The scenario spectra remain separate and preserve the physical identity of each source’s earthquake across the period range. The report nomenclature defines two envelopes over the scenario set E through a single construction: the per-period maximum of the scenario ordinates for the reported statistic. The upper-fractile envelope, reported as MCE (84%), is

Sa(84%)(Tn)=maxe∈EQ(0.84∣e),	(3.26)

a maximum over values that does not select a scenario. The mean envelope, reported as MCE, applies the same construction to the scenario means, so its ordinates likewise belong to no individual scenario, and neither envelope identifies a controlling magnitude–distance pair. The comparison with the probabilistic hazard superimposes the deterministic envelopes MCE and MCE (84%) on the available mean uniform-hazard spectra and uses the mean spectrum for TR=10,000 years as the comparison level at the selected periods.

The distribution of each scenario integrates three sources of uncertainty, two epistemic and one aleatory. Epistemic rupture uncertainty is represented by the explicit physical variants adopted for the hypocentral depth, the dip, the rupture style, and the plane orientation; the NR realizations receive the same weight 1/NR. Epistemic model uncertainty represents the differences among the GMM branches admitted for the tectonic regime of the scenario; each branch enters with the weight vg defined by the adopted logic tree. Aleatory variability represents the record-to-record dispersion for a fixed rupture realization and GMM branch, and in component k=(r,g) it is expressed through the logarithmic standard deviation σk of branch g, evaluated for realization r.

The mixture of 3.23 represents the three sources through its parameters. The combination wk=vg/NR simultaneously incorporates the rupture variation and the model weighting; the dispersion among the medians μk characterizes the two epistemic contributions, while each σk contributes the aleatory variability of its component. The resulting distribution is characterized through the fractiles of 3.24, and each component preserves the correspondence among the rupture geometry, the source-to-site distances, and the GMM branch that originated its prediction.

The results of the deterministic assessment correspond to the maximum horizontal component of Sa(Tn) at 5% of critical damping on reference rock, VS30=760 m/s. The mean is presented for each scenario; the MCE and the MCE (84%) are obtained through independent per-period maxima. The table presents the spectral ordinates of the scenarios and their MCE envelopes; the graphical superposition of those spectra and the available mean uniform-hazard spectra is provided in the online results identified at the beginning of this section. The governing scenario is identified separately for each period and statistic, and that identification represents the changes of controlling source along the spectrum, so each envelope preserves the identity of the scenario contributing its ordinate at each period.

Table 3.2: Deterministic scenarios for site CFD, as declared in the calculation specifications. e is the scenario identifier and TRT the tectonic region type that selects its ground-motion logic tree. Mw is the moment magnitude of the rupture. Repi is the epicentral distance (km), the median over the rupture variants. Depth is the hypocentral depth (km), reported as the min–max range across the declared rupture variants. Strike, Dip, and Rake are the rupture-plane angles (°); Rake lists the discrete values declared across variants. MSR is the magnitude scaling relation that sizes the rupture, coded as AH = AllenHayesInterfaceBilinear, L14 = Leonard2014_SCR, STF = StrasserInterface, STS = StrasserIntraslab, THR = ThingbaijamReverseFault, WC94 = WC1994. Aspect is the rupture length-to-width aspect ratio (min–max range across variants). Variants is the number of declared rupture variants of the scenario.

| e | TRT | Mw | Repi | Depth | Strike | Dip | Rake | MSR | Variants |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| S1 | SCC | 6.5 | 100 | 15 | 324 | 46 | 100 | WC94 | 1 |
| S2 | SCC | 4.5 | 5 | 2.5 | 112 | 80 | 90 | WC94 | 1 |

Table 3.3: Maximum horizontal spectral accelerations Sa(Tn) [g] for the deterministic scenarios at site CFD, with VS30 = 760 m/s and 5% critical damping. Scenario columns report conditional means; MCE and MCE (84%) report the envelopes of the conditional means and 84th percentiles, respectively. Tn is the oscillator period in seconds; Tn=0 corresponds to PGA.

| Tn | S1 | S2 | MCE | MCE (84%) |
| --- | --- | --- | --- | --- |
| 0.0 | 0.070 | 0.237 | 0.237 | 0.375 |
| 0.1 | 0.215 | 0.840 | 0.840 | 1.352 |
| 0.2 | 0.151 | 0.394 | 0.394 | 0.620 |
| 0.5 | 0.070 | 0.089 | 0.089 | 0.141 |
| 1.0 | 0.033 | 0.020 | 0.033 | 0.052 |
| 2.0 | 0.013 | 0.004 | 0.013 | 0.020 |
| 5.0 | 0.003 | 0.000 | 0.003 | 0.004 |

Table 3.4: Peak ground acceleration of the deterministic scenarios for site CFD, by site condition. Each scenario e reports its mean PGA (g); the MCE rows report the mean and 84th-percentile deterministic envelope of the scenarios. Each remaining column is a site condition identified by its time-averaged shear-wave velocity VS30 (m/s).

| e | 180 | 270 | 360 | 560 | 800 | 1250 | 1500 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| S1 | 0.105 | 0.094 | 0.087 | 0.078 | 0.072 | 0.073 | 0.074 |
| S2 | 0.248 | 0.270 | 0.271 | 0.254 | 0.245 | 0.276 | 0.293 |
| MCE | 0.248 | 0.270 | 0.271 | 0.254 | 0.245 | 0.276 | 0.293 |
| MCE (84%) | 0.384 | 0.424 | 0.426 | 0.404 | 0.391 | 0.447 | 0.480 |

The deterministic scenario spectra and their comparison with the probabilistic demand are developed in the Seismic Hazard Assessment annex.

## 3.5	Seismic Record Selection

The time histories constitute the seismic demand used as input to the dynamic deformation analyses and represent simultaneously its amplitude, duration, and frequency content. PGA characterizes the peak amplitude; the significant duration, the number of cycles near the peak, and the distribution of energy across frequencies describe additional characteristics that contribute to the accumulated deformation of slopes and embankments of cohesionless materials (Bray & Travasarou, 2007; Kramer, 1997). Record selection establishes a suite of motions whose spectral demand is compatible with the target band, whose temporal characteristics remain available to the dynamic models, and whose source events, stations, and records are identified.

The selected motions must be compatible with the hazard controlling the site, with the adopted target spectrum, and with the response variables of the dynamic model, and must represent the relevant record-to-record variability (NEHRP Consultants Joint Venture, 2011). The candidate set is delimited by magnitude and source–site distance windows tied to the scenarios controlling the hazard, identified from the hazard model and its disaggregation; the selection criteria further comprise the tectonic environment, the site conditions, component availability, usable frequency content, and record quality (Baker & Cornell, 2006). Within that set, spectral shape is evaluated by agreement with the target demand over the period range of the analysis – not through a separate conditional-spectrum or epsilon-based rule – and at most one record per event is retained. The target spectrum corresponds to the design ordinate of the demand adopted for the site – the mean or a design fractile, per the demand – and the lower and upper envelopes to low and high fractiles of that same demand; the envelopes define the admissible range around the target for the matched suite. The grid includes Tn=0 as the PGA ordinate and the positive periods of the analysis. The evaluation retains the identifiers of the event, the station, the record, and the source network or database, together with the intensity measures used to characterize the suite. No additional filters are applied by tectonic environment or by station VS30.

Deterministic channel mapping classifies the three recorded directions into the canonical components H1, H2, and UP, and the rotation of the two horizontals to their principal axes defines H1 and H2, with the rotation angle recorded per record. Spectral matching and verification are performed on H1, so that the record table, the intensity measures, and the reported spectra correspond to a single definition of horizontal motion. The procedure does not modify the frequency content of the records to reproduce the target spectrum: the adjustment is limited to the amplitude of the retained modes and to one scale factor per record, so that each history preserves the phases, the sequence of cycles, and the non-stationarity of the recorded motion – the properties that contribute to the accumulated deformation of slopes and embankments – and the compatibility of the suite with the target band is achieved in the spectral mean and in the containment of the individual spectra.

Empirical mode decomposition introduced intrinsic mode functions as data-adaptive components for nonlinear and non-stationary time series (Huang et al., 1998). The adopted procedure uses variational mode decomposition (VMD), which represents a non-stationary signal as a set of modes with compact frequency bands and a residue (Dragomiretskiy & Zosso, 2014); the canonical histories of the full record are decomposed component by component. For the H1 component of record i,

xi(t)=m=1Kixi(m)(t)+ri(t),	(3.27)

where xi(t) is the recorded acceleration, xi(m)(t) is mode m of record i, Ki is the number of modes, and ri(t) is the residue. The procedure excludes IMF1, the low-frequency component associated with drift and noise, and defines the retained set Mi with the remaining modes; the adjustment applies bounded amplitude multipliers bi(m) per record,

xi(t;bi)=m∈Mi​bi(m) xi(m)(t),	(3.28)

and preserves the central frequencies and the phases of the retained modes. Compatibility is evaluated with the pseudo-spectral acceleration operator

Sa,j[z]=Sa[z](Tj,ξ),	(3.29)

where z(t) is an acceleration history, Tj is a target period, and ξ=5% is the damping ratio; sij(bi)=Sa,j​xi(bi) is the reconstructed ordinate of record i. With yj, lj, and uj as the target and the lower and upper envelopes at Tj, the target-normalized misfit of the record is

RMSEi(bi)=1Jj=1Jsij(bi)−yjyj21/2.	(3.30)

and the out-of-band excursion of the record at Tj is

vij(bi)=max​lj−sij(bi)lj, sij(bi)−ujuj, 0.	(3.31)

The multipliers are obtained by minimizing, with bi(m)=bi,0(m) eθi(m) and within their bounds, the regularized objective

Li(θi)=RMSEi2(θi)+λenv 1Jj=1Jvij2(θi)+λmov 1|Mi|m∈Mi​(θi(m))2,	(3.32)

where bi,0(m) is the initial value of the multiplier: the first term reduces the misfit with respect to the target, the second penalizes the excursions outside the band, and the third limits unnecessary movement of the retained multipliers. The minimization applies a deliberately bounded number of iterations, so that the adjustment remains close to the recorded motion. After the modal adjustment, the factor

ei=t​xi2(t)t​xi2(t;bi)1/2,  yi(t)=eixi(t;bi),	(3.33)

normalizes the quadratic energy of the reconstructed signal with respect to the recorded history; the normalization preserves the discrete quadratic norm of the record’s acceleration after reconstruction, and the effective contribution of mode m is ei bi(m) xi(m)(t). This stage removes the low-frequency component associated with drift and noise and maintains the temporal structure of the modes that represent the motion at the reference condition (Verri Kozlowski, 2026b).

Each reconstructed and normalized history receives a positive coefficient ci,

Yi(t)=ciyi(t)=cieim∈Mi​bi(m)xi(m)(t),	(3.34)

so that Yi(t) is the final H1 component employed in the analyses. The coefficients ci are determined jointly, as a bounded quadratic problem over the complete suite, to reproduce the target spectral mean and to contain the individual spectra within the prescribed band. The objective function is

minci>0 &1Jj=1Jwjrj2+λBNJi=1Nj=1Jvij2,&wj=λD,rj<0,1,rj≥0,	(3.35)

where the residual of the suite mean and the suite mean itself at each target period are

rj=Sa(Tj)−Sat(Tj)Sat(Tj),  Sa(Tj)=1Ni=1NciSa,j[yi],	(3.36)

and the out-of-band excursion is evaluated on the scaled spectra ciSa,j[yi] with the same form as in the modal adjustment. Here, N is the number of records, J is the number of target periods, Sat is the target spectrum, λB weights the containment of the individual spectra, and λD≥1 weights the deficits of the suite mean. The value λD=1 produces a symmetric weighting of positive and negative residuals.

The final verification computes the relative RMSE of Sa with respect to Sat, the ratio of the suite-mean PGA to the target PGA, the fraction of record–period ordinates contained by the envelopes, and the range of the coefficients ci. The delivered suite retains the acceleration, velocity, and displacement histories used in the dynamic analyses, the cumulative and scalar intensity measures, the significant durations, the PSA spectra, and the provenance metadata of events and stations. This chapter reports the table of selected records and the PSA comparison of H1 with the target spectrum.

Table 3.5: Selected ground motions for site CFD. IDi identifies the record and the Event column the originating earthquake; Mw is the moment magnitude, dimensionless; Repi is the epicentral distance, in km; PGA is the peak ground acceleration, in g; IA is the Arias intensity, CAV the cumulative absolute velocity and CAV5 the thresholded cumulative absolute velocity, the three in mm/s; and ci is the scale coefficient applied to each record of the suite after modal reconstruction and energy normalization, dimensionless. The total change relative to the original recording combines those three operations. Intensity measures are reported for the H1 component of each record, on which the spectral matching and the verification are performed.

| IDi | Event | Mw | Repi | PGA | IA | CAV | CAV5 | ci |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 7fc739394f8514e7 | 3 km W of Cushing, Oklahoma | 5.00 | 5.0 | 0.473 | 524 | 3,090 | 1,790 | 1.237 |
| 0dbcb847262d1446 | 12 km NNW of Coalinga, California | 5.18 | 4.3 | 0.397 | 913 | 4,070 | 3,090 | 0.935 |
| 504ad228238b7aaf | 3 km ENE of Novi di Modena, Italy | 4.90 | 6.8 | 0.386 | 426 | 2,970 | 1,680 | 1.095 |
| 5ee93d2d7e1f3ec8 | 20100903T163717Z | 5.11 | 27.9 | 0.344 | 717 | 6,770 | 3,250 | 0.969 |
| b12abf045d51ff12 | 14 km ESE of Christchurch, New Zealand | 4.84 | 15.1 | 0.316 | 478 | 4,240 | 2,260 | 1.137 |
| 4368bec7b5408390 | 40 km ENE of Amberley, New Zealand | 5.22 | 5.0 | 0.308 | 243 | 1,550 | 848 | 0.997 |
| 9e55774aadb09712 | 8km NE of Gonzales, CA | 4.81 | 9.6 | 0.282 | 381 | 2,730 | 1,550 | 1.330 |
| 7f9008ec725865ad | 8km SW of Holtville, CA | 5.01 | 7.7 | 0.276 | 139 | 1,570 | 544 | 0.992 |
| 51206aef7e9998b1 | 4 km W of Gemlik, Turkey | 5.00 | 11.5 | 0.275 | 254 | 2,840 | 940 | 1.271 |
| 11e3599a48322bdc | 4km NE of Westmorland, CA | 4.90 | 3.7 | 0.272 | 410 | 3,680 | 1,870 | 1.039 |
| f55d48cdd87f7346 | 15 km NE of Oía, Greece | 5.10 | 29.0 | 0.261 | 418 | 5,310 | 1,910 | 1.158 |
| bc3928a34bfbd2d0 | 20100903T164849Z | 4.95 | 22.1 | 0.237 | 287 | 2,670 | 1,280 | 1.047 |
| 4cd6aa9d1cc15096 | 20100903T163842Z | 5.16 | 45.5 | 0.230 | 513 | 7,030 | 2,380 | 1.052 |
| b9ccad75fdeaa8fb | 3 km SSW of Ferndale, California | 5.20 | 30.0 | 0.209 | 276 | 2,560 | 1,340 | 1.098 |
| 71ba579f3aaba372 | 31 km SE of Puli, Taiwan | 6.30 | 100.7 | 0.202 | 459 | 7,590 | 1,980 | 1.736 |
| c7da6a6286087e55 | 6 km ESE of Managua, Nicaragua | 5.20 | 5.7 | 0.196 | 282 | 3,430 | 1,480 | 0.871 |
| 06caa95385e8f518 | 33 km SE of Puli, Taiwan | 6.20 | 102.1 | 0.189 | 352 | 6,860 | 1,450 | 2.106 |
| 4238698ef454ef45 | 15 km E of Christchurch, New Zealand | 5.19 | 9.4 | 0.187 | 146 | 2,280 | 644 | 1.346 |
| bcb0006cec5e8f77 | 28 km SW of Ölüdeniz, Turkey | 5.90 | 123.9 | 0.186 | 409 | 6,200 | 1,920 | 0.939 |
| f98cc58424a371f4 | 4 km ESE of Prebbleton, New Zealand | 4.80 | 9.0 | 0.181 | 185 | 2,120 | 857 | 1.107 |
| 15770e935a5882b9 | 15 km SE of Christchurch, New Zealand | 5.00 | 12.0 | 0.176 | 228 | 2,670 | 1,190 | 0.992 |
| 56e233ac014318d9 | 19760911T163110Z | 5.20 | 6.1 | 0.174 | 203 | 1,830 | 1,090 | 1.093 |
| 25cbaa1db812694c | 1 km SSE of Prebbleton, New Zealand | 5.20 | 8.8 | 0.170 | 186 | 2,230 | 936 | 1.108 |
| c9af922310a1caba | 0 km E of Rolleston, New Zealand | 5.10 | 1.3 | 0.164 | 174 | 2,360 | 839 | 1.525 |
| 24540f0a9a3fc39d | South Island of New Zealand | 4.86 | 30.0 | 0.164 | 329 | 4,820 | 1,760 | 1.445 |
| 3a1a681c09756f5e | 20111223T010053Z | 5.24 | 8.1 | 0.162 | 168 | 2,220 | 857 | 1.100 |
| 03a89db298564354 | 5 km WNW of Fylí, Greece | 5.90 | 262.9 | 0.148 | 253 | 3,340 | 1,250 | 1.022 |
| dccd23395fb5ff0f | The 1992 Big Bear, California Earthquake | 6.46 | 115.5 | 0.143 | 354 | 6,130 | 1,850 | 1.429 |
| 467bdc929d351885 | South Island of New Zealand | 4.98 | 12.7 | 0.141 | 339 | 4,420 | 1,870 | 1.206 |
| 172516bb571001fa | 10 km ESE of Christchurch, New Zealand | 5.21 | 24.5 | 0.125 | 305 | 5,100 | 1,570 | 1.212 |

The selected records and their verifications are presented in the Seismic Record Selection annex.

# 4	Design Earthquakes

## 4.1	Site-Response

The design ground motions are defined for the VS30 conditions evaluated at the site from the spectral demand at the surface. The assessment represents these effects through two alternative estimates of the surface spectral demand and combines the corresponding probability distributions to define the design demand at each structural period, return period, and VS30 condition. The GMM logic tree is evaluated in the hazard model for the project VS30 conditions (180, 270, 360, 560, 800, 1250, 1500 m/s). Each model incorporates its empirical site term when estimating Sa(Tn,VS30); the logic-tree weights represent the adopted epistemic alternatives, and the aleatory variability of each model is integrated into the exceedance curves. The assessment therefore retains the same source and ground-motion characterization used in the rock assessment; the site terms are evaluated for each VS30 value analyzed. The GMM site term and the external model represent mean ergodic responses derived from sets of records.

The demand calculated for the reference condition Vref=760 m/s constitutes the input to the NGA-East ergodic site-amplification model (ST20), developed by Stewart et al. (2020) and Hashash et al. (2020). For each period Tn, condition VS30, and realization of the input PGA pga*, the factor F is modeled as a lognormal random variable whose natural logarithm has mean μlnF and standard deviation σlnF,

lnF∼N​μlnF, σlnF2,	(4.1)

where μlnF is the conditional mean log-amplification and σlnF is the total dispersion of the model. The mean combines the adjustment between the 760 and 3000 m/s references, the linear term dependent on VS30, and the nonlinear term dependent on pga*, and the dispersion is expressed as

σlnF2=σL2+σI2+σNL2,	(4.2)

where σL corresponds to the linear site term, σI to the change between reference horizons, and σNL to the intensity-dependent nonlinear term. The formulation of the components and the treatment of the reference are detailed below.

Sao(Tn) and PGAo denote the ordinates calculated by OpenQuake with the GMMs for the adopted reference condition; this condition is 760 m/s in the current assessment and may be 3000 m/s when the input corresponds to the hard-rock reference. For each period and return period, the distribution of Sao is represented by a lognormal surrogate calibrated with the arithmetic mean and the seven quantiles published by the hazard calculation: the mean is preserved exactly and the logarithmic deviation σo is fitted to the quantiles,

lnSao∼N​lnμo−σo22, σo2,	(4.3)

where μo=E[Sao] is the reported arithmetic mean. The published quantiles of the direct assessment correspond to this surrogate and not to the raw fractiles of the logic tree. The ordinate obtained with ST20 is

Sas​Tn,VS30=F​Tn,VS30,PGAo Sao​Tn.	(4.4)

The assessment considers separately the distribution of Sao, obtained with the GMMs for the VS30 analyzed, and the distribution of Sas, obtained with ST20. The resulting distribution is defined as a finite mixture of the two; its formulation and its statistics are presented in the uncertainty section.

The factor F of 4.4 follows the ergodic site-amplification framework developed for central and eastern North America. Stewart et al. (2020) establish the linear response and the reference-condition change; Hashash et al. (2020) formulate the intensity-dependent nonlinear modification. The model is expressed with respect to a 3000 m/s hard-rock condition. Its composite log-amplification f at a site condition VS30, for the oscillator period Tn and the input PGA pga*, is the sum of three components:

f(Tn,VS30,pga*)=lnF760(Tn,VS30)+lnFV(Tn,VS30)+lnFnl(Tn,VS30,pga*).	(4.5)

To transform an input at Vref=760 m/s, the calculation applies the exact difference between the composite model evaluated at the target condition and at the reference condition, for the same period and input intensity:

μlnF(Tn,VS30,pga*)=f(Tn,VS30,pga*)−f(Tn,Vref,pga*).	(4.6)

VS30 is the travel-time-averaged shear-wave velocity in the uppermost 30 m, Tn is the oscillator period, and pga* is the input PGA. In each evaluation of the composite model, Fcomp=F760FVFnl; the factor applied from 760 m/s is therefore the ratio between Fcomp at the target condition and at the reference condition. The linear term FV represents the stiffness change with respect to the reference condition and varies with VS30 and Tn; it equals unity at 760 m/s and decreases gradually toward stiffer conditions. The term F760 links the 760 m/s reference to the model’s native 3000 m/s hard rock; it depends on the period, generally exceeds unity, and weights reference profiles with impedance contrast and with velocity gradient. The difference in 4.6 preserves that weighting in both evaluations, including its transition for velocities below 600 m/s.

The term Fnl represents the variation of amplification with ground-motion intensity and depends on VS30, Tn, and the input PGA pga*. The formulation uses a period-dependent reference – 760 m/s for Tn<0.4 s and 3000 m/s for longer periods – and converts the input PGA at 760 m/s to the hard-rock reference through pga3000*=pga760*/2.275 (Hashash et al., 2020; Stewart et al., 2020). At low intensities the response approaches the linear regime; as pga* increases, the term reproduces the reduction in amplification associated with nonlinear soil response. The balance between FV and Fnl makes it possible to represent amplification at intermediate and long periods and reduction at short periods for softer soils, while the transformation approaches unity when the target condition coincides with the reference.

The dispersion of 4.2 accompanies the same evaluation by period, velocity, and intensity. σL represents the dispersion of the linear term; σI enters the conversion from the 3000 m/s reference and vanishes when the input is already expressed at 760 m/s; and σNL=σf2ln[(pga3000*+f3)/f3] represents the dispersion of the nonlinear term. The coefficients and the transitions with Tn and VS30 are those tabulated by Stewart et al. (2020).

The 760 and 3000 m/s references serve distinct roles in the calculation. The former corresponds to the B/C boundary of the NEHRP classification and is a customary reference condition in United States ground-motion models and design criteria; moreover, much of the recorded data supporting these models concentrates approximately between 200 and 800 m/s. The latter represents the shallow crystalline basement of central and eastern North America used by NGA-East and by regional hard-rock assessments. Stewart et al. (2020) establish the conversion between the two references while maintaining compatibility with the empirical data and the site classes. The model is calibrated primarily for VS30 between approximately 200 and 1500–2000 m/s and applies gradual transitions toward the limits of its domain.

The evaluation with ST20 is performed period by period and is conditioned on the PGA of the same realization through the nonlinear term of F. In logarithmic scale, 4.4 is expressed as lnSas=lnSao+lnF. For a component k of the distribution of Sao and a realization PGAo=pga*, with q=lnpga*, σk is the standard deviation of lnSao(Tn) in the component, ρ=Corr​lnSao(Tn),lnPGAo is the within-event correlation between the spectral ordinate and the PGA, and σlnF=σlnF(Tn,VS30,eq) is the standard deviation of lnF for the period, the site condition, and the conditioning PGA pga*=eq; the conditional variance of lnSas is

Var​lnSas∣k,q=1−ρ2σk2+σlnF2.	(4.7)

The dependence between Sao(Tn) and F is incorporated through the PGA of the same realization, which conditions the nonlinear term of ST20. Once the component k and that PGA are fixed, the model does not provide a parameter representing an additional residual correlation between the spectral ordinate and the amplification factor. The evaluation therefore adopts conditional independence between the two residuals, avoiding the introduction of an uncalibrated covariance. For the deterministic scenarios, the spectral demand at the reference condition is represented by the analytic mixture of 3.23. In each component k, (μP,k,σP,k) are the mean and standard deviation of lnPGAo, while (μk,σk) are the mean and standard deviation of lnSao(Tn). Conditional on the component and on a realization PGAo=pga*, with q=lnpga*, and with μlnF=μlnF(Tn,VS30,eq) and σlnF=σlnF(Tn,VS30,eq) evaluated for the period, the site condition, and the conditioning PGA, the ordinate obtained with ST20 has the distribution

lnSas∣(k,q)∼N​μk(q),𝜍k2(q).	(4.8)

Its conditional mean is the mean of the spectral ordinate conditioned on the PGA of the same realization, plus the mean log-amplification,

μk(q)=μk+ρσkσP,k(q−μP,k)+μlnF.	(4.9)

and its conditional variance adds the variance of the log-amplification factor to the part of the spectral variance that the conditioning PGA does not explain, under the conditional independence adopted above:

𝜍k2(q)=1−ρ2σk2+σlnF2.	(4.10)

The cumulative distribution function of Sas is obtained by integrating its conditional distribution with respect to q=lnpga* in each component, where y>0 is a spectral-acceleration value in the same units as Sas, wk is the component weight, μk(q) and 𝜍k(q) are, respectively, the conditional mean and standard deviation of lnSas defined in 4.9 and 4.10, and Φ and φ are the standard-normal cumulative distribution function and density:

Gs(y)=P​Sas≤y=k​wk−∞∞Φ​lny−μk(q)𝜍k(q)φ​q−μP,kσP,kdqσP,k.	(4.11)

The quantiles of Gs define the deterministic fractiles of Sas, and its mean is evaluated with the corresponding conditional moments of 3.25. In the probabilistic assessment, the surface spectral demand is characterized, for each period Tn, return period TR, and VS30 condition, by two probability distributions. The first corresponds to the site response that the ground-motion models (GMMs) evaluate directly for that VS30 value, represented by the lognormal surrogate of 4.3; the second results from applying ST20 to the demand calculated at the reference condition Vref=760 m/s. The random variables Sao and Sas represent the resulting spectral accelerations, and Go(y) and Gs(y) their respective cumulative distribution functions. The cumulative distribution function of the resulting random variable, Sa, is

G(y)=P​Sa≤y=αGo(y)+(1−α)Gs(y),  0≤α≤1.	(4.12)

In the absence of site-specific evidence that would assign greater representativeness to one of the two distributions, α=0.5 is adopted, without interpreting it as a calibrated value. This coefficient may be revised through a site-response study that contrasts Go and Gs with observations or validated simulations of the relation between the rock and surface demands, and estimates α in the interval [0,1] through an explicit calibration criterion. In the expressions that follow, μo=E[Sao] and μs=E[Sas] are the arithmetic means of the two component distributions, μ=E[Sa] is the arithmetic mean of the resulting distribution – all expressed on the natural spectral-acceleration scale, not on the logarithmic scale – and Q is the quantile function of the resulting distribution. The arithmetic mean of the resulting distribution is

μ=αμo+(1−α)μs.	(4.13)

its probability-p quantile, obtained by inverting its cumulative distribution function, is

Q(p)=inf{y:G(y)≥p},  0<p<1.	(4.14)

and its variance is

Var(Sa)=αVar(Sao)+(1−α)Var(Sas)+α(1−α)(μo−μs)2.	(4.15)

The first two terms weight the variances of the component distributions, while the last corresponds to the contribution associated with the difference between their means. The mixture defined above specifies marginal distributions for each period but does not determine the dependence between periods. In operations requiring jointly distributed ordinates – for example PGA, Sa(1.3Tn), and Sa(1.5Tn) for the displacement evaluation – that dependence is represented with the model of Baker and Jayaram (2008). For the range Tmin>0.109 s, with Tmin=min(Ti,Tj) and Tmax=max(Ti,Tj),

ρ(Ti,Tj)=1−cos​π2−0.366lnTmaxmax(Tmin,0.109).	(4.16)

When Tmin≤0.109 s, the correlation is obtained from the corresponding branches of the Baker and Jayaram formulation (2008, Eqs. 5–6). The model is applicable between 0.01 and 10 s and is independent of magnitude and distance.

Table 4.1: Peak ground acceleration, PGA [cm/s2], for site CFD at VS30 = 800 m/s. TR is the return period, in years, and PT is the probability of at least one exceedance during the exposure interval of the calculation, as a percentage. The remaining columns are the demand statistics: those headed by a probability level p hold the quantile Q(p), and the one headed mean holds the mean, both in the units stated. The MCE row reports the deterministic envelope over the scenarios of each statistic: the envelope of the scenario means in the mean column and of the scenario quantiles in the columns headed by p; it carries no return period, so TR and PT do not apply.

| TR | PT | 0.50 | mean | 0.84 | 0.90 | 0.95 |
| --- | --- | --- | --- | --- | --- | --- |
| 100 | 39.3 | 8 | 8 | 11 | 12 | 14 |
| 200 | 22.1 | 15 | 16 | 22 | 24 | 28 |
| 500 | 9.5 | 32 | 35 | 49 | 55 | 65 |
| 1000 | 4.9 | 55 | 61 | 86 | 98 | 117 |
| 2000 | 2.5 | 91 | 101 | 143 | 163 | 194 |
| 2500 | 2.0 | 106 | 118 | 167 | 191 | 227 |
| 5000 | 1.0 | 162 | 181 | 258 | 296 | 352 |
| 10000 | 0.5 | 236 | 265 | 379 | 435 | 520 |
| MCE | — | 184 | 241 | 383 | 474 | 617 |

Table 4.2: Peak ground acceleration by return period and site condition (siteID: CFD). Columns identified by VS30 (m/s) represent the site conditions. The TR rows (years) report the mean probabilistic PGA (g), and the MDE (84%) row reports the 0.84 quantile of the PGA for the return period of the MDE. The MCE and MCE (84%) rows report the deterministic envelope at its mean and 84th percentile, respectively, for the same site conditions.

| TR | 180 | 270 | 360 | 560 | 800 | 1250 | 1500 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 100 | 0.013 | 0.012 | 0.011 | 0.009 | 0.008 | 0.009 | 0.009 |
| 200 | 0.025 | 0.022 | 0.020 | 0.018 | 0.016 | 0.017 | 0.017 |
| 500 | 0.055 | 0.048 | 0.044 | 0.039 | 0.036 | 0.037 | 0.037 |
| 1,000 | 0.094 | 0.082 | 0.076 | 0.068 | 0.062 | 0.064 | 0.065 |
| 2,000 | 0.147 | 0.132 | 0.123 | 0.111 | 0.103 | 0.106 | 0.108 |
| 2,500 | 0.166 | 0.152 | 0.142 | 0.129 | 0.120 | 0.124 | 0.126 |
| 5,000 | 0.234 | 0.225 | 0.214 | 0.196 | 0.185 | 0.191 | 0.194 |
| 10,000 | 0.313 | 0.314 | 0.307 | 0.284 | 0.270 | 0.280 | 0.285 |
| MDE (84%) | 0.441 | 0.449 | 0.439 | 0.406 | 0.386 | 0.402 | 0.412 |
| MCE | 0.248 | 0.270 | 0.271 | 0.254 | 0.245 | 0.276 | 0.293 |
| MCE (84%) | 0.384 | 0.424 | 0.426 | 0.404 | 0.391 | 0.447 | 0.480 |

Table 4.3: Design earthquakes in terms of pseudo-spectral acceleration Sa(Tn) [cm/s2] for site CFD, for return periods from 100 to 10000 yr, oscillator periods from 0 to 5 s, the site condition VS30 = 800 m/s, and the statistic p = mean. When the report covers more than one site, a leading siteID column identifies the site. The identifying columns are Tn, the oscillator period, in seconds, with Tn=0 representing PGA; VS30, the shear-wave velocity of the evaluated condition, in m/s; and p, the reported statistic, the ensemble mean or the quantile probability level, dimensionless. Each remaining column is headed by a return period TR, in years, and holds the Sa(Tn) ordinates in the units stated.

| Tn | VS30 | 100 | 200 | 500 | 1000 | 2000 | 2500 | 5000 | 10000 | p |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 0.000 | 800 | 8 | 16 | 35 | 61 | 101 | 118 | 181 | 265 | mean |
| 0.050 | 800 | 12 | 26 | 65 | 119 | 206 | 243 | 390 | 597 | mean |
| 0.075 | 800 | 15 | 32 | 74 | 133 | 225 | 263 | 414 | 624 | mean |
| 0.100 | 800 | 18 | 35 | 79 | 137 | 227 | 264 | 410 | 610 | mean |
| 0.120 | 800 | 17 | 34 | 74 | 128 | 210 | 245 | 378 | 560 | mean |
| 0.150 | 800 | 17 | 32 | 68 | 116 | 189 | 220 | 338 | 499 | mean |
| 0.180 | 800 | 17 | 30 | 63 | 106 | 172 | 198 | 303 | 446 | mean |
| 0.200 | 800 | 16 | 29 | 60 | 100 | 161 | 186 | 284 | 417 | mean |
| 0.220 | 800 | 15 | 27 | 54 | 90 | 145 | 167 | 255 | 374 | mean |
| 0.250 | 800 | 14 | 24 | 48 | 79 | 125 | 144 | 220 | 323 | mean |
| 0.280 | 800 | 13 | 23 | 44 | 71 | 113 | 130 | 198 | 291 | mean |
| 0.300 | 800 | 13 | 22 | 42 | 67 | 106 | 123 | 186 | 274 | mean |
| 0.350 | 800 | 11 | 19 | 37 | 59 | 92 | 106 | 161 | 238 | mean |
| 0.400 | 800 | 10 | 18 | 33 | 53 | 82 | 94 | 143 | 211 | mean |
| 0.450 | 800 | 10 | 16 | 30 | 47 | 73 | 84 | 128 | 189 | mean |
| 0.500 | 800 | 9 | 15 | 28 | 43 | 66 | 76 | 115 | 170 | mean |
| 0.600 | 800 | 7 | 12 | 22 | 34 | 52 | 60 | 90 | 133 | mean |
| 0.700 | 800 | 6 | 10 | 19 | 29 | 44 | 50 | 75 | 111 | mean |
| 0.750 | 800 | 5 | 9 | 18 | 27 | 41 | 47 | 69 | 102 | mean |
| 0.850 | 800 | 5 | 8 | 16 | 24 | 36 | 41 | 60 | 89 | mean |
| 0.900 | 800 | 4 | 8 | 15 | 23 | 34 | 38 | 57 | 83 | mean |
| 1.000 | 800 | 4 | 7 | 13 | 20 | 30 | 34 | 51 | 74 | mean |
| 1.250 | 800 | 3 | 5 | 10 | 16 | 23 | 26 | 39 | 57 | mean |
| 1.500 | 800 | 2 | 4 | 8 | 13 | 19 | 21 | 31 | 46 | mean |
| 1.750 | 800 | 2 | 3 | 7 | 11 | 16 | 18 | 26 | 38 | mean |
| 2.000 | 800 | 2 | 3 | 6 | 9 | 14 | 16 | 23 | 33 | mean |
| 2.500 | 800 | 1 | 2 | 4 | 6 | 10 | 11 | 16 | 24 | mean |
| 3.000 | 800 | 1 | 1 | 3 | 5 | 7 | 8 | 12 | 18 | mean |
| 3.500 | 800 | 1 | 1 | 2 | 4 | 6 | 7 | 10 | 15 | mean |
| 4.000 | 800 | 0 | 1 | 2 | 3 | 5 | 5 | 8 | 12 | mean |
| 4.500 | 800 | 0 | 1 | 2 | 3 | 4 | 5 | 7 | 10 | mean |
| 5.000 | 800 | 0 | 1 | 1 | 2 | 3 | 4 | 6 | 9 | mean |

Table 4.4: Site amplification factors AF, dimensionless, of the design demand for site CFD relative to the VS30=760 m/s reference condition, for return periods from 100 to 10000 yr, oscillator periods from 0 to 5 s, the site condition VS30 = 800 m/s, and the statistic p = mean. When the report covers more than one site, a leading siteID column identifies the site. The identifying columns are Tn, the oscillator period, in seconds, with Tn=0 representing PGA; VS30, the shear-wave velocity of the evaluated condition, in m/s; and p, the reported statistic, the ensemble mean or the quantile probability level, dimensionless. Each remaining column is headed by a return period TR, in years, and holds the corresponding AF factor.

| Tn | VS30 | 100 | 200 | 500 | 1000 | 2000 | 2500 | 5000 | 10000 | MCE | p |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 0.000 | 800 | 0.99 | 1.00 | 1.00 | 1.00 | 1.00 | 1.00 | 1.00 | 1.01 | 1.01 | mean |
| 0.050 | 800 | 0.97 | 0.98 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | mean |
| 0.075 | 800 | 0.97 | 0.98 | 0.98 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | mean |
| 0.100 | 800 | 0.97 | 0.98 | 0.98 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | mean |
| 0.120 | 800 | 0.97 | 0.98 | 0.98 | 0.98 | 0.99 | 0.99 | 0.99 | 0.99 | 0.99 | mean |
| 0.150 | 800 | 0.97 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | mean |
| 0.180 | 800 | 0.97 | 0.97 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | mean |
| 0.200 | 800 | 0.97 | 0.97 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | mean |
| 0.220 | 800 | 0.97 | 0.97 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.97 | mean |
| 0.250 | 800 | 0.97 | 0.97 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.97 | mean |
| 0.280 | 800 | 0.97 | 0.97 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | mean |
| 0.300 | 800 | 0.97 | 0.97 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | mean |
| 0.350 | 800 | 0.96 | 0.97 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | mean |
| 0.400 | 800 | 0.96 | 0.97 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | mean |
| 0.450 | 800 | 0.96 | 0.97 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | mean |
| 0.500 | 800 | 0.96 | 0.97 | 0.97 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | mean |
| 0.600 | 800 | 0.95 | 0.97 | 0.97 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | mean |
| 0.700 | 800 | 0.95 | 0.96 | 0.97 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | mean |
| 0.750 | 800 | 0.95 | 0.96 | 0.97 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | mean |
| 0.850 | 800 | 0.95 | 0.97 | 0.97 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | mean |
| 0.900 | 800 | 0.95 | 0.96 | 0.97 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | mean |
| 1.000 | 800 | 0.95 | 0.97 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | mean |
| 1.250 | 800 | 0.95 | 0.96 | 0.97 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | mean |
| 1.500 | 800 | 0.95 | 0.96 | 0.97 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | mean |
| 1.750 | 800 | 0.95 | 0.96 | 0.97 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | mean |
| 2.000 | 800 | 0.95 | 0.96 | 0.97 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | mean |
| 2.500 | 800 | 0.95 | 0.96 | 0.97 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | mean |
| 3.000 | 800 | 0.95 | 0.96 | 0.97 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | mean |
| 3.500 | 800 | 0.95 | 0.96 | 0.97 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | mean |
| 4.000 | 800 | 0.95 | 0.97 | 0.97 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | mean |
| 4.500 | 800 | 0.95 | 0.97 | 0.97 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | mean |
| 5.000 | 800 | 0.96 | 0.97 | 0.97 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | 0.98 | mean |

The spectra by site condition and the amplification factors are developed in the Seismic Hazard Assessment annex.

## 4.2	Seismic Design Criteria for Slopes

The seismic design of tailings storage facilities is based on the two-level performance framework consolidated by dam-safety practice: an Operating Basis Earthquake (OBE), which the facility must withstand without operational interruption, and a Safety Evaluation Earthquake (SEE), under which it must not release tailings. ICOLD Bulletin 148 formalizes this framework for embankment structures (Australian National Committee on Large Dams, 2012; International Commission on Large Dams, 2016), and the USACE Engineer Regulation ER 1110-2-1806 expresses it in terms of the OBE and the Maximum Design Earthquake (MDE) (U.S. Army Corps of Engineers, 1995).

Three international frameworks implement these two performance levels for tailings storage facilities according to the consequence class of the facility: the Global Industry Standard on Tailings Management (GISTM) (Global Tailings Review (ICMM, UNEP, PRI), 2020), the Canadian Dam Association (CDA) guidelines (Canadian Dam Association, 2019; Canadian Dam Association (CDA), 2021), and the Australian National Committee on Large Dams (ANCOLD) guidelines (Australian National Committee on Large Dams (ANCOLD), 2019). The consequence class, from Low to Extreme, reflects the potential severity of a failure in terms of population at risk, anticipated loss of life, and environmental and socio-economic impacts, governs the stringency of the seismic criteria, and sets progressively more stringent annual exceedance probabilities (AEPs) for the design earthquakes. GISTM defines five consequence classes, CDA five consequence classifications, and ANCOLD six consequence categories, with three gradations, High C, High B and High A, within its High category. The classes and the design-earthquake AEPs of each framework are tabulated in Tables 6.1, 6.2 and 6.3.

Each framework designates the design earthquake in its own terms. GISTM specifies a single design ground motion for each consequence class and lifecycle stage, with the Maximum Credible Earthquake (MCE) evaluated in parallel and governing whenever it produces the higher demand (2020). CDA adopts the SEE as the design basis, admits the MCE as a declared alternative to the probabilistic level for high-consequence facilities, and allows risk-based departures for lower classes during transitional closure stages provided the post-closure requirements are ultimately met; its tabulated levels are targets for initial consideration and consultation between owner and regulator, and the designer of record and the owner may adopt more stringent levels to further reduce risk, or less stringent ones where justified (2021). ANCOLD assigns an OBE and an SEE to each consequence category: a uniform OBE of 1/500 AEP together with an SEE that ranges from 1/1,000 AEP up to the greater of the MCE and the 1/10,000 AEP event (84th percentile) for the Extreme category (2019), in line with mining-sector regulatory guidance that assigns design return periods of 10,000 years or longer to extreme-consequence structures (Seismic Permanent Displacements for Tailings Storage Facilities and Waste Rock Dumps, n.d.).

For a given consequence class, the design earthquake also varies with the lifecycle stage. During construction, partial-height embankments are checked against the OBE as a minimum, and against the SEE for high-consequence facilities or in high-seismicity regions. During operation, the stage with the largest stored volumes and the highest risk profile, the differentiation by consequence class is greatest: operational AEPs range from 1/200 (GISTM, Low) or 1/100 (CDA) to 1/10,000 for Extreme facilities. Closure and post-closure criteria are specific to each framework. GISTM retains the operational criteria through active-care closure and sets a 1/10,000 AEP for all classes during passive-care post-closure (Global Tailings Review (ICMM, UNEP, PRI), 2020). CDA retains criteria that depend on the consequence classification through closure and passive care: closure under active care with regular monitoring retains the levels of the construction, operation and transition stages, and passive care, which is distinct from abandonment of the facility, begins only once a steady-state condition has been demonstrated by accumulated experience and monitoring; any risk-based transition must be justified (Canadian Dam Association, 2019; Canadian Dam Association (CDA), 2021). ANCOLD adopts for post-closure the SEE of the applicable category and requires it to be reassessed at closure when the hazard, the condition of the dam, or its consequences change (Australian National Committee on Large Dams (ANCOLD), 2019).

In this report, the MDE is represented by the probabilistic spectrum for a 10,000-year return period, whereas the MCE is represented by the deterministic envelope. GISTM requires comparison of the MDE and MCE for the Extreme class during operations and active-care closure, and for every class during passive-care post-closure (Global Tailings Review (ICMM, UNEP, PRI), 2020). For CDA, the alternative between the probabilistic level and the MCE is set against the MDE for the Extreme class during construction, operation, and transition, and for the Very High and Extreme classes during closure and passive care (Canadian Dam Association (CDA), 2021). ANCOLD assigns the MDE to the High A category and, for the Extreme category, requires the greater of the MDE and MCE (Australian National Committee on Large Dams (ANCOLD), 2019).

Design ground motions for slopes are reported by lifecycle stage: operation, closure, and post-closure. The design earthquake that applies to each stage, whether the OBE, the SEE, or the PCE, is the one that each standard assigns to the consequence class of the facility in Tables 6.1, 6.2, and 6.3: ANCOLD designates it as the OBE or the SEE of the consequence category, GISTM as the design ground motion of the class and stage, and CDA as the Earthquake Design Ground Motion (EDGM) of the consequence classification. For each site condition, the probabilistic demand of a criterion is derived by linking its prescribed return period to the available uniform hazard spectrum (UHS); where the criterion is defined between two return periods, the design demand is the average of the demands evaluated at both, and the UHS is taken at its mean, except for the ANCOLD Extreme-category closure criterion, which is taken at the 84th percentile. Where the Extreme-class criterion invokes the MCE, the MCE (mean) and MCE (84%) series accompany the design spectra. The design PGA and design spectra are reported by framework, consequence class, lifecycle stage, and site condition.

The verification of the slopes under those design earthquakes follows the practice that ICOLD and FEMA frame for dams and embankments through successive tiers of analysis including pseudostatic stability checks, simplified estimates of permanent deformation, and dynamic analyses where warranted by the consequences of failure, anticipated response, or complexity of the failure mechanism (Federal Emergency Management Agency, 2005; International Commission on Large Dams, 2016). Within this framework, the Newmark method provides a deformation-based assessment that complements the limit-equilibrium analysis. The pseudostatic seismic coefficient is a project-specific value rather than a universal value assigned to a particular structure type. USACE manuals EM 1110-2-1902 and EM 1110-2-2100 include pseudostatic analysis among the methods applicable to dams and earthworks and address the sliding block for estimating permanent seismic deformation. Selection of the coefficient considers the site-specific seismic hazard, potential failure mechanism, and project performance criteria, so the coefficient results from the conditions of each project instead of a single value applicable to all of them (U.S. Army Corps of Engineers, 2003, 2005).

Two further references relate the pseudostatic verification to the permanent deformation. NCHRP Report 611 formulates the seismic analysis of slopes and transportation infrastructure in terms of displacement-based performance and uses simplified Newmark correlations to relate demand to permanent deformation (Anderson et al., 2008), and Eurocode 8 ties the pseudostatic action to the design seismic acceleration and the consequence class and admits Newmark displacement calculations when the ratio between the critical acceleration and the design acceleration justifies a deformation-based verification (European Committee for Standardization, 2004). These references provide the framing and the comparison criteria for the coefficients of this report; their indicative values serve that comparison, and the displacement objective defined for the project governs the coefficients themselves.

That objective is expressed as an allowable permanent displacement relative to the slope height. This report evaluates the coefficients at four damage thresholds of the relative permanent displacement, Da/H = 0.1, 0.4, 1.0, 2.5%: the crest-settlement ratios derived from ninety case histories of earthquake damage to embankment dams and associated with the Operational, Damage, Life Safety and Collapse limit states of the Italian dam code NTD14 (Aliberti et al., 2019). Their denominator, the reference height, includes the embankment height and the thickness of the deformable foundation and is adopted here as the slope height for normalization. The seismic coefficient tables are presented for these four thresholds and the coefficient figures shade the intervals they delimit. Chapter 5.2 describes the derivation of the coefficients from the allowable displacement.

Table 4.5: Operational design earthquakes in terms of peak ground acceleration PGA [cm/s2] by standard (GISTM, CDA, ANCOLD) and consequence class, for the site condition VS30 = 800 m/s at site CFD. siteID, present when the table gathers more than one site, identifies the site; Standard is the guideline that sets the criterion, Class the consequence classification of the facility and Stage the project stage covered by the table. TR is the return period of the criterion, in years; where the criterion combines two return periods, the cell shows their half-sum. VS30 is the shear-wave velocity of the evaluated site condition, in m/s. p identifies the statistic of the uniform-hazard demand adopted by the criterion: the mean or the quantile indicated. PGA is the design peak ground acceleration, expressed in the unit indicated; where the criterion is defined over two return periods, it is the average of the demands evaluated at both.

| Standard | Class | Stage | TR | VS30 | p | PGA |
| --- | --- | --- | --- | --- | --- | --- |
| ANCOLD | Low | Operation | 500 | 800 | mean | 35 |
| ANCOLD | Significant | Operation | 500 | 800 | mean | 35 |
| ANCOLD | High C | Operation | ½ × (500 + 1,000) | 800 | mean | 48 |
| ANCOLD | High B | Operation | ½ × (500 + 1,000) | 800 | mean | 48 |
| ANCOLD | High A | Operation | ½ × (500 + 1,000) | 800 | mean | 48 |
| ANCOLD | Extreme | Operation | ½ × (500 + 1,000) | 800 | mean | 48 |
| CDA | Low | Operation | 100 | 800 | mean | 8 |
| CDA | Significant | Operation | ½ × (100 + 1,000) | 800 | mean | 35 |
| CDA | High | Operation | 2,500 | 800 | mean | 118 |
| CDA | Very High | Operation | ½ × (2,500 + 10,000) | 800 | mean | 191 |
| CDA | Extreme | Operation | 10,000 | 800 | mean | 265 |
| GISTM | Low | Operation | 200 | 800 | mean | 16 |
| GISTM | Significant | Operation | 1,000 | 800 | mean | 61 |
| GISTM | High | Operation | 2,500 | 800 | mean | 118 |
| GISTM | Very High | Operation | 5,000 | 800 | mean | 181 |
| GISTM | Extreme | Operation | 10,000 | 800 | mean | 265 |

Table 4.6: Seismic design criteria of the GISTM standard at the Operation stage for CFD. Class is the consequence classification; TR is the governing annual-exceedance criterion expressed as a return period (yr) — where the standard sets the criterion between two return periods, the cell shows both and reports the average of their accelerations. Cells report the design PGA (g) that the criterion selects from the probabilistic hazard for VS30=180,270,360,560,800,1250,1500 m/s.

| Class | TR | 180 | 270 | 360 | 560 | 800 | 1250 | 1500 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Low | 200 | 0.025 | 0.022 | 0.020 | 0.018 | 0.016 | 0.017 | 0.017 |
| Significant | 1,000 | 0.094 | 0.082 | 0.076 | 0.068 | 0.062 | 0.064 | 0.065 |
| High | 2,500 | 0.166 | 0.152 | 0.142 | 0.129 | 0.120 | 0.124 | 0.126 |
| Very High | 5,000 | 0.234 | 0.225 | 0.214 | 0.196 | 0.185 | 0.191 | 0.194 |
| Extreme | 10,000 | 0.313 | 0.314 | 0.307 | 0.284 | 0.270 | 0.280 | 0.285 |

Table 4.7: Closure design earthquakes in terms of peak ground acceleration PGA [cm/s2] by standard (GISTM, CDA, ANCOLD) and consequence class, for the site condition VS30 = 800 m/s at site CFD. siteID, present when the table gathers more than one site, identifies the site; Standard is the guideline that sets the criterion, Class the consequence classification of the facility and Stage the project stage covered by the table. TR is the return period of the criterion, in years; where the criterion combines two return periods, the cell shows their half-sum. VS30 is the shear-wave velocity of the evaluated site condition, in m/s. p identifies the statistic of the uniform-hazard demand adopted by the criterion: the mean or the quantile indicated. PGA is the design peak ground acceleration, expressed in the unit indicated; where the criterion is defined over two return periods, it is the average of the demands evaluated at both.

| Standard | Class | Stage | TR | VS30 | p | PGA |
| --- | --- | --- | --- | --- | --- | --- |
| ANCOLD | Low | Closure | 1,000 | 800 | mean | 61 |
| ANCOLD | Significant | Closure | 1,000 | 800 | mean | 61 |
| ANCOLD | High C | Closure | 2,000 | 800 | mean | 101 |
| ANCOLD | High B | Closure | 5,000 | 800 | mean | 181 |
| ANCOLD | High A | Closure | 10,000 | 800 | mean | 265 |
| ANCOLD | Extreme | Closure | 10,000 | 800 | 0.84 | 379 |
| CDA | Low | Closure | 1,000 | 800 | mean | 61 |
| CDA | Significant | Closure | 2,500 | 800 | mean | 118 |
| CDA | High | Closure | ½ × (2,500 + 10,000) | 800 | mean | 191 |
| CDA | Very High | Closure | 10,000 | 800 | mean | 265 |
| CDA | Extreme | Closure | 10,000 | 800 | mean | 265 |

Table 4.8: Post-closure design earthquakes in terms of peak ground acceleration PGA [cm/s2] by standard (GISTM, CDA, ANCOLD) and consequence class, for the site condition VS30 = 800 m/s at site CFD. siteID, present when the table gathers more than one site, identifies the site; Standard is the guideline that sets the criterion, Class the consequence classification of the facility and Stage the project stage covered by the table. TR is the return period of the criterion, in years; where the criterion combines two return periods, the cell shows their half-sum. VS30 is the shear-wave velocity of the evaluated site condition, in m/s. p identifies the statistic of the uniform-hazard demand adopted by the criterion: the mean or the quantile indicated. PGA is the design peak ground acceleration, expressed in the unit indicated; where the criterion is defined over two return periods, it is the average of the demands evaluated at both.

| Standard | Class | Stage | TR | VS30 | p | PGA |
| --- | --- | --- | --- | --- | --- | --- |
| GISTM | Low | Post-Closure | 10,000 | 800 | mean | 265 |
| GISTM | Significant | Post-Closure | 10,000 | 800 | mean | 265 |
| GISTM | High | Post-Closure | 10,000 | 800 | mean | 265 |
| GISTM | Very High | Post-Closure | 10,000 | 800 | mean | 265 |
| GISTM | Extreme | Post-Closure | 10,000 | 800 | mean | 265 |

The design criteria by standard and consequence classification are developed in the Seismic Design Criteria annex.

## 4.3	Seismic Design Criteria for Structures

Seismic demand for conventional structures is established in accordance with ASCE/SEI 7-22 from the hazard and site-response spectra developed in Part I. Section 11.4.7 refers to the site-specific procedures of Sections 21.1 and 21.2; where those procedures are applied, the design spectrum and its parameters are determined in accordance with Sections 21.3 and 21.4 (Minimum Design Loads and Associated Criteria for Buildings and Other Structures, 2022, Sections 11.4.7, 21.1–21.4). The probabilistic component of the MCER spectrum is evaluated, for each period Tn and VS30 condition, from the resulting random variable Sa(Tn), whose cumulative distribution function G is defined in 4.12. For each return period TR, the ordinate considered is its arithmetic mean μ=E[Sa], defined in 4.13, and the associated annual exceedance rate is 1/TR, in accordance with 3.4. The pairs (μ,1/TR) corresponding to the available return periods constitute the input curve to the risk-targeted adjustment procedure of Section 21.2.1.

The risk-targeted adjustment represents the fragility prescribed by Section 21.2.1 through the random variable Cx, the spectral collapse capacity associated with a candidate ordinate x:

lnCx∼N​μlnC,σlnC2.	(4.17)

In this expression, μlnC and σlnC are the mean and the standard deviation of lnCx, respectively, and for each x

μlnC=lnx−Φ−1(0.10)σlnC,  σlnC=0.60,

so that P[Cx≤x]=0.10; Cx represents the generic fragility adopted by the risk-targeted adjustment procedure and not a capacity calculated for the structures at the site (Luco et al., 2007; Minimum Design Loads and Associated Criteria for Buildings and Other Structures, 2022, Section 21.2.1). In the risk calculation, the intensity measure I of 3.2 corresponds to Sa(Tn), and the annual collapse rate associated with the candidate ordinate x is

λC(x)=0∞λI(i*) fCx(i*) di*,	(4.18)

where fCx is the density function of the capacity defined in 4.17, and λI(i*) represents the curve determined by the pairs (μ,1/TR) of the preceding paragraph. The probabilistic ordinate corresponds to the value of x that satisfies

1−exp​−50 λC(x)=0.01.	(4.19)

and this evaluation is performed separately for each Tn and VS30 condition.

ASCE/SEI 7-22 requires the MCER spectral ordinates to represent the maximum response in the horizontal plane. Where the GMM provides the geometric mean or a similar measure of the two horizontal components, Section 21.2 establishes directional factors of 1.20 for Tn≤0.2 s, 1.25 for Tn=1.0 s, and 1.30 for Tn≥10 s (Minimum Design Loads and Associated Criteria for Buildings and Other Structures, 2022, Section 21.2). To establish a common definition among the horizontal GMMs, the hazard model transforms the RotD50, GMRotI50, and random-horizontal components to geometric mean before combining the branches; the models defined for the vertical component do not enter this combination. The ordinates expressed as geometric mean are subsequently converted to maximum response in the horizontal plane through the directional factors indicated.

The contribution of the scenarios to the deterministic component of the MCER spectrum is obtained, for each Tn and VS30, as

Sa(84%)(Tn)=maxe∈EQ(0.84∣e).	(4.20)

where E gathers the seismic scenarios included in the analysis. The ordinates Sa(Tn) of Table 21.2-1 constitute the prescribed lower limit for the deterministic MCER spectrum corresponding to the site class used for the evaluated VS30 condition, and the deterministic component is established, for each Tn, as

max​Sa(84%)(Tn),Sa(Tn).	(4.21)

The site-specific MCER ordinate is the lesser of the probabilistic and the deterministic components (Minimum Design Loads and Associated Criteria for Buildings and Other Structures, 2022, Section 21.2.3). The probabilistic component is the solution of 4.19, expressed through λC−1, the inverse function of the collapse rate defined in 4.18, so that, for each Tn and VS30 condition,

SaM(Tn)=min​λC−1​−ln0.9950,max​Sa(84%)(Tn),Sa(Tn).	(4.22)

In accordance with Section 21.3, the design spectral accelerations are obtained from the MCER ordinates of 4.22 through

Sa(Tn)=23SaM(Tn).	(4.23)

Where the design ground motions are determined through the site-specific procedure, in accordance with Section 21.3, the design acceleration parameters are calculated as (Minimum Design Loads and Associated Criteria for Buildings and Other Structures, 2022, Section 21.4)

SDS&=0.9maxT∈[0.2,5] sSa(T),SD1&=max​0.9maxT∈[1,T*] s(T Sa(T)),Sa(1 s),T*&=2 s,VS30>442 m/s,5 s,VS30≤442 m/s.	(4.24)

and the corresponding MCER parameters are recovered from the design values through

SMS=1.5SDS,  SM1=1.5SD1.	(4.25)

The chapter retains the site-specific MCER spectra for the evaluated VS30 conditions, with one ordinate per period of the hazard curves; the results report the MCER PGA and the maximum spectral ordinates per site condition.

Section 21.2.2 bounds the deterministic spectrum from below by the tabulated values of Table 21.2-1 – the Sa(Tn) component of 4.21 – defined by site class from T=0 to 10 s and including PGA, and admits an exception: where the probabilistic spectrum remains below those values at all periods, the deterministic motions are not calculated (Minimum Design Loads and Associated Criteria for Buildings and Other Structures, 2022, Section 21.2.2). Verifying that exception consists of comparing the probabilistic spectrum with the tabulated values at each evaluated site condition. The 80% floor of Section 21.2.3 is anchored to the USGS Seismic Design Geodatabase and its application is limited to that database’s coverage (Minimum Design Loads and Associated Criteria for Buildings and Other Structures, 2022, Section 21.2.3).

In addition to the site-specific design spectrum, the report includes the code-form design spectrum of ASCE/SEI 7-22 Section 11.4.5, built piecewise from the parameters SDS and SD1. With T0=0.2 SD1/SDS and TS=SD1/SDS,

Sa(Tn)=SDS0.4+0.6 TnT0,Tn<T0,SDS,T0≤Tn≤TS,SD1Tn,Tn>TS,	(4.26)

with the ordinates in g. Outside the reach of the Section 22 maps no long-period transition TL is adopted; the SD1/Tn branch extends to the end of the period grid (Minimum Design Loads and Associated Criteria for Buildings and Other Structures, 2022, Section 11.4.5).

Table 4.9: ASCE/SEI 7-22 seismic design parameters for site CFD, by site condition, obtained from the risk-targeted MCER spectrum. The spectral ordinates correspond to the mixture of the two site-demand estimates. Each row is a site condition and VS30 is its shear-wave velocity, in m/s. SaM(0) is the MCER ordinate at zero period; SMS and SM1 are the MCER acceleration parameters; SDS and SD1 are the design acceleration parameters; these four ordinates and SaM(0) are in g. T0=0.2,SD1/SDS and TS=SD1/SDS are the corner periods of the design spectrum, in seconds.

| VS30 | SaM(0) | SMS | SM1 | SDS | SD1 | T0 | TS |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 180 | 0.144 | 0.213 | 0.082 | 0.142 | 0.055 | 0.077 | 0.385 |
| 270 | 0.136 | 0.210 | 0.069 | 0.140 | 0.046 | 0.066 | 0.328 |
| 360 | 0.129 | 0.202 | 0.058 | 0.134 | 0.038 | 0.057 | 0.286 |
| 560 | 0.117 | 0.178 | 0.041 | 0.119 | 0.027 | 0.046 | 0.229 |
| 800 | 0.110 | 0.157 | 0.033 | 0.105 | 0.022 | 0.042 | 0.208 |
| 1,250 | 0.113 | 0.136 | 0.031 | 0.091 | 0.021 | 0.046 | 0.228 |
| 1,500 | 0.115 | 0.133 | 0.030 | 0.089 | 0.020 | 0.046 | 0.229 |

The structural design spectra and their parameters are developed in the Seismic Design Criteria annex.

# 5	Ground-Motion Design Parameters

## 5.1	Dynamic Properties of Slopes

Flexible sliding-block models account for the dynamic response of the potential sliding mass through spectral acceleration evaluated at a period proportional to its fundamental period, so each slope geometry–material combination needs Ts, which is derived from the geometry and the depth-dependent small-strain shear stiffness, described by Go, mo, and VSo; the mean values of Ts and VS30 provide the dynamic inputs to the permanent-displacement models. The fundamental period of the potential sliding mass is estimated from the first mode of the truncated inhomogeneous shear-beam model of Dakoulas and Gazetas (1985) as

Ts=4πHa1(2−mo)VSo,	(5.1)

where H=Hs/(1−λo) is the height of the truncated wedge from the apex of the extended slopes to the base, Hs is the slope height, VSo is the basal shear-wave velocity associated with Go, mo is the inhomogeneity factor governing the shear-modulus profile, and a1 is the first modal root of the characteristic equation. The modal root depends jointly on mo and the truncation ratio λo, which geometric similarity gives as

λo=bbmax,	(5.2)

where b and bmax are the berm and base widths, respectively. The equivalent truncated section in the Dakoulas–Gazetas model (1985) is specified by the height Hs, slope ratio s, and truncation ratio λo; with tanβ=1/s, where β is the slope angle, the berm width is given by

b=2Hss1/λo−1.	(5.3)

and the base width is

bmax=b+2Hss.	(5.4)

For each profile realization, the basal shear-wave velocity is

VSo=gGoγsat(kb)1/2,	(5.5)

where Go is the fitted small-strain shear modulus at the base, g is the acceleration of gravity, and γsat(kb) is the saturated unit weight of the basal layer, indexed by kb; all quantities are expressed in consistent units. The depth dependence of small-strain shear stiffness is represented for each realization by the power-law profile

G(z)=GozHsmo,	(5.6)

where z is depth below the crest, Go is the fitted shear modulus at the base (z/Hs=1), and mo is obtained from a logarithmic fit to the layer moduli Gm(k); the characteristic equation corresponds to the power law with depth measured from the apex of the extended slopes and normalized by H (1985), so evaluating a1 with the exponent fitted from the crest is an approximation. The layer moduli come from the soil classification: the USCS classification assigned to layer k selects its soil family and the associated set of J(k) small-strain shear-modulus correlations compiled by Ishihara (1996), and the layer modulus is taken as their arithmetic mean,

Gm(k)=1J(k)j=1J(k)A(j)Fe(k,j)OCR(k)m1(k)prefn(j)pm(k)prefn(j).	(5.7)

Here A(j) and n(j) are tabulated correlation parameters, Fe(k,j) is the void-ratio function, m1(k) is the overconsolidation exponent, pm(k) is the layer-averaged effective octahedral normal stress, and pref=100 kPa is the reference pressure. Under at-rest conditions, the layer-averaged effective octahedral normal stress pm(k) (1968; 1972) is

pm(k)=1+2K03ℓ=1k−1γ(ℓ)h(ℓ)+γ(k)h(k)2,	(5.8)

where K0 is the at-rest lateral earth pressure coefficient, γ(ℓ) and h(ℓ) are the unit weight adopted for the groundwater condition and the thickness of layer ℓ, and ℓ<k denotes the overlying layers. The layer overconsolidation ratio is OCR(k)=max[(pm(k)+POP)/pm(k),1], where POP is the preconsolidation pressure; for fine-grained soils, m1(k)=fIP(IP(k)), whereas for sands and gravels m1(k)=0 and the OCR multiplier is therefore unity. The void ratio e0(k) enters all three soil families through Fe(k,j), which the correlations compiled by Ishihara (1996) define in terms of e0(k) and Ce(j), with the index jSS75 identifying the Shibata–Soelarno formulation (1975):

Fe(k,j)=Ce(j)−e0(k)1+e0(k),j=jSS75,Ce(j)−e0(k)21+e0(k),j≠jSS75.	(5.9)

The shear-wave velocity of layer k then follows from

VS(k)=gGm(k)γsat(k)1/2,	(5.10)

where Gm(k) is the adopted layer modulus and γsat(k) is its saturated unit weight; all quantities are expressed in consistent units.

Table 5.1: Parameters of the small-strain stiffness formulations for gravels, sands, and fine-grained soils, used in expression 5.7 with pm(k) and pref in kPa and Gm(k) in MPa.

| Formulation | Family | Reference material | Author | A | Ce | n |
| --- | --- | --- | --- | --- | --- | --- |
| HR63A | Sands | Angular-grain crushed sand | Hardin & Richart (1963) | 3.27 | 2.973 | 0.50 |
| HR63R | Sands | Round-grain Ottawa sand | Hardin & Richart (1963) | 7.00 | 2.174 | 0.50 |
| IW78 | Sands | Several sands | Iwasaki et al.(1978) | 9.00 | 2.174 | 0.38 |
| KO80 | Sands | Toyoura sand | Kokusho (1980) | 8.40 | 2.173 | 0.50 |
| LO93 | Sands | Ticino sands | Lo Presti et.al (1993) | 7.10 | 2.270 | 0.43 |
| SS75 | Sands | Several sands | Shibata-Soelarno (1975) | 42.00 | 0.670 | 0.50 |
| YR84 | Sands | Several sands | Yu-Richart (1984) | 7.00 | 2.173 | 0.50 |
| HB68 | Fines | Several undisturbed NC Clays | Hardin & Black (1968) | 3.27 | 2.973 | 0.50 |
| KU82C | Fines | Undisturbed NC Clay | Kokusho et al.(1982) | 0.14 | 7.320 | 0.60 |
| MW72B | Fines | Reconstituted NC Bentonite | Marcuson & Wahls (1972) | 0.45 | 4.400 | 0.50 |
| MW72K | Fines | Reconstituted NC Kaoline | Marcuson & Wahls (1972) | 4.50 | 2.973 | 0.50 |
| ZU78A | Fines | Clay remolded IP=0-50% | Zen-Umehara (1978) | 2.00 | 2.973 | 0.50 |
| ZU78B | Fines | Clay remolded IP=0-50% | Zen-Umehara (1978) | 3.00 | 2.973 | 0.50 |
| ZU78C | Fines | Clay remolded IP=0-50% | Zen-Umehara (1978) | 4.00 | 2.973 | 0.50 |
| GO87 | Gravels | Gravel | Goto et al.(1987) | 1.22 | 2.170 | 0.85 |
| KE81G | Gravels | Rounded Gravel | Kokusho-Esashi (1981) | 8.40 | 2.170 | 0.60 |
| KE81R | Gravels | Crushed Rock | Kokusho-Esashi (1981) | 13.00 | 2.170 | 0.55 |
| NI85 | Gravels | Gravel | Nishio et al.(1985) | 9.36 | 2.170 | 0.44 |
| PR81 | Gravels | Balast | Prange (1981) | 7.23 | 2.970 | 0.38 |
| TA87 | Gravels | Gravel | Tanaka et al.(1987) | 3.08 | 2.170 | 0.60 |

For each geometry–material combination, the analysis generates N synthetic realizations of the layered profile, and each of Go, mo, VSo, and VS30 is summarized by its mean and selected marginal fractiles; for the mean and for each reported fractile, a1 and Ts are evaluated from the corresponding mo and VSo values, and the estimates calculated from the mean parameter values provide the dynamic properties used in the displacement analysis. VS30 is the travel-time-averaged shear-wave velocity in the uppermost 30 m:

VS30=30i​h30(i)VS(i)+max(30−Hs,0)Vref.	(5.11)

In this expression, h30(i) is the portion of layer i within the uppermost 30 m and VS(i) is its shear-wave velocity; when Hs<30 m, the reference velocity Vref is assigned to the remaining thickness.

Table 5.2: Material scenarios representative of most of the universe of slope and geostructure materials — among them tailings storage facilities (TSF) and waste rock dumps (WRD) — used in the Newmark displacement and fundamental-period analyses, with the slope materials classified per the Unified Soil Classification System (USCS).

| IDm | USCS | TSF Zone |
| --- | --- | --- |
| U1 | ML MH | Fine Tailings (Slimes, Pond) |
| U2 | SP SM | Coarse Tailings Beach / Upstream Shell |
| U3 | SP SM ML MH | Transitional Zone (Beach Margin / Intermediate Tailings) |
| U4 | GP GW | Rockfill Buttress / Downstream Shell |
| U5 | GP GW SP SM | Downstream Shell with Granular Filter or Transition Layer |
| U6 | GP GW ML MH | Downstream Shell with Fines-Enriched Transition / Filter |
| U7 | CL CH | Core Zone (Impervious Core / Cutoff Trench) |
| U8 | CL CH ML MH | Core Zone with Silty-Clay Transition (Core Margin / Fine Fill) |

Table 5.3: Fundamental periods in [s] and shear moduli in [MPa] for a slope of 50 m height, for material classifications (USCS) representative of tailings storage facilities (TSF) and waste rock dumps (WRD). IDm identifies the material scenario and USCS the classification of the slope materials. Hs is the slope height and b the geometric parameter, both in m; s is the slope ratio (tanβ=1/s) and λo the truncation ratio, both dimensionless; Go is the shear modulus of the profile at z/Hs=1, in MPa, and mo the exponent of its power law, dimensionless; a1 is the first modal root, dimensionless; VSo is the basal shear-wave velocity and VS30 the travel-time-averaged shear-wave velocity in the uppermost 30 m, both in m/s; and Ts≈T1 is the fundamental period, in seconds.

| IDm | USCS | Hs | b | s | λo | mo | a1 | Go | VSo | VS30 | Ts |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| U1 | ML MH | 50 | 108 | 2.75 | 0.282 | 0.457 | 3.3303 | 157.8 | 287.2 | 194.9 | 0.593 |
| U2 | SP SM | 50 | 108 | 2.75 | 0.282 | 0.479 | 3.3699 | 213.4 | 324.7 | 218.0 | 0.526 |
| U3 | SP SM ML MH | 50 | 108 | 2.75 | 0.282 | 0.471 | 3.3553 | 183.4 | 303.3 | 205.2 | 0.562 |
| U4 | GP GW | 50 | 108 | 2.75 | 0.282 | 0.553 | 3.5114 | 523.6 | 476.6 | 300.5 | 0.361 |
| U5 | GP GW SP SM | 50 | 108 | 2.75 | 0.282 | 0.532 | 3.4700 | 346.2 | 398.9 | 253.8 | 0.431 |
| U6 | GP GW ML MH | 50 | 108 | 2.75 | 0.282 | 0.516 | 3.4391 | 291.4 | 367.0 | 236.6 | 0.467 |
| U7 | CL CH | 50 | 108 | 2.75 | 0.282 | 0.407 | 3.2443 | 142.2 | 272.5 | 191.6 | 0.621 |
| U8 | CL CH ML MH | 50 | 108 | 2.75 | 0.282 | 0.429 | 3.2814 | 149.7 | 280.2 | 194.0 | 0.606 |

## 5.2	Performance-Based Seismic Coefficient

Pseudostatic seismic design of slopes requires a horizontal coefficient representing earthquake loading on the sliding mass. In this report the coefficient is derived from displacement-based performance: the Newmark permanent displacement Dn is the slope-deformation performance measure, and the coefficient kmax is the lowest yield coefficient ky consistent with a performance objective defined by the allowable displacement Da and the target maximum probability pe that Dn exceeds Da. The normalized coefficient kh expresses kmax as a percentage of the site-condition PGA after site response is accounted for in each geometry–material combination, and the coefficients are reported by geometry, material and seismic demand. For the slopes considered, Dn is estimated probabilistically by combining empirical regression models within a lognormal framework.

The horizontal pseudostatic coefficient is derived in this assessment from the allowable permanent displacement Da of the potentially sliding mass (Bray & Travasarou, 2009; Macedo et al., 2018). The seismic demand and the fundamental periods established in the preceding chapters allow the Dn(ky) relations between the Newmark permanent displacement and the yield coefficient to be computed; their inversion yields kmax, and its normalization by the PGA transformed to the VS30 of each geometry–material combination yields kh, so that the result traceably links the deformation objective to the horizontal action employed in the stability verification. The yield acceleration ay represents the acceleration level that mobilizes the available resistance along the potential failure mechanism, and its dimensionless form is ky=ay/g; for each allowable displacement and target exceedance probability, the analysis determines the ky threshold that satisfies the performance criterion, and that threshold is kmax, the coefficient applied in the pseudostatic limit-equilibrium verification.

In the Newmark sliding-block method (Newmark, 1965), the potentially sliding wedge is represented as a rigid block resting on an inclined plane: relative motion begins when the driving acceleration exceeds the yield acceleration ay=kyg and continues until the relative velocity returns to zero, and the permanent displacement is the sum of those episodes over the duration of the earthquake motion, obtained by double integration of the acceleration excess. The extension of the procedure to dams and embankments (Makdisi & Seed, 1978) derived the equivalent acceleration of the sliding mass from its dynamic response and is the direct antecedent of the flexible formulations. The adopted empirical relations represent the accumulated displacement statistically through two idealizations: rigid-block models relate the displacement to measures of the base excitation, and flexible-block models additionally incorporate the dynamic response of the mass through Ts and the spectral acceleration evaluated at a period proportional to Ts.

The displacement calculation uses the seismic demand and the fundamental periods established in Chapter 5.1. For each geometry, material and seismic demand – the probabilistic spectrum of each evaluated return period and the MCE scenario – a joint sample of the intensity measures required by the rigid-block and flexible formulations is constructed; that sample is common to all models, so their differences represent the displacement formulation rather than incompatible seismic demands. Two inputs feed that sample. The probabilistic input for each return period is the reference-rock UHS, which for 10,000 years represents the MDE, and the MCE input is the rock spectrum of each scenario; both retain the complete distribution of the rock demand, and both are defined for VS30=Vref=760 m/s. For each geometry and material scenario, the spectral ordinates and the PGA are transformed to the corresponding VS30 through the ST20 amplification model (Hashash et al., 2020; Stewart et al., 2020).

At the site condition of each scenario, the joint sample comprises PGA, Sa(1.3Ts), and Sa(1.5Ts). The three measures are represented through empirical marginals in lnSa and a Gaussian copula with the full inter-period correlation matrix (Baker & Jayaram, 2008), and the samples are recentered to preserve the mean of each amplified marginal; in each realization, the three intensities remain paired, and each displacement formulation uses the measures entering its regression. The Arias intensity used by JB07 and SR08 completes the set of intensity measures; it is estimated for each realization from the PGA (Verri Kozlowski, 2023), and the relation is applied deterministically, so that each PGA realization determines a single value of IA and the displacement sample propagates the PGA variability.

For each scenario, 30 values of ky are evaluated, logarithmically spaced between 0.01 and max(PGA,0.80), where PGA is the mean site-condition PGA of the scenario. That interval establishes the computed range of the Dn(ky) relations, over which the formulations are evaluated and the inversion to kmax operates.

Each active formulation estimates the Newmark permanent displacement (1965) of the sliding mass from the yield acceleration and the intensity measures of its regression, and all of them express the positive displacement Dn, in centimeters, through

Dn=exp​μlnD+ϵσlnD,  ϵ∼N(0,1),	(5.12)

where μlnD and σlnD are the mean and standard deviation of lnDn defined by each model, and ϵ is a standard-normal residual. Some source formulations contain a discrete branch of zero or negligible displacement; the implemented evaluation uses exclusively the positive lognormal branch. In every formulation, ky, PGA, and Sa are expressed in units of g – the acceleration of gravity – IA in m/s, and Ts in seconds; the Arias intensity is derived from the PGA of each realization according to 6.3, and the reference magnitude assigned to each seismic demand is applied to its geometry–material combinations. The published form of each formulation is reproduced in Appendix 6.5. The performance-based seismic coefficient is defined by

kmax(pe∣Da)=infky:P[Dn(ky)>Da]≤pe.	(5.13)

where pe is the target probability that Dn exceeds Da: kmax is the smallest ky for which the probability of exceeding the allowable displacement is at most pe. The normalized coefficient, reported as a percentage of the PGA [% of PGA], is calculated using the site-condition PGA transformed to the VS30 of the geometry–material combination evaluated for each demand:

kh=100 kmaxPGA(VS30).	(5.14)

kmax is expressed in units of g and kh as a percentage of the PGA of the corresponding site condition. These two quantities express the displacement criterion as the horizontal action of the pseudostatic verification.

The five formulations are evaluated individually and combined into the three sets that the tables and figures identify as IDn: rigid, flexible and ensemble. The displacement model provides individual realizations for AM88, JB07, SR08, BT07, and a fifth formulation selected by the tectonic context: BM17 for projects with subduction control and BM19 for projects with shallow crustal control. The overall design set, identified as ensemble, combines AM88, JB07, SR08, BT07, and the active BM branch with equal weights; the rigid family combines AM88, JB07, and SR08, and the flexible family combines BT07 and the active BM branch. The rigid family thus relates the displacement to measures of the base excitation, the flexible family additionally incorporates the dynamic response of the sliding mass through Ts, and the ensemble is the design set that combines both. For each ky, the displacements of a family are summarized from the weighted empirical distribution of the realizations of its models.

All models receive the same joint sample of PGA and spectral accelerations, and a single realization of ϵ is shared across the models and across all values of ky; each formulation scales that residual through its own σlnD, and the sampled PGA is retained with each realization so that the inversion preserves the pairing between displacement and seismic demand. The realizations of Dn are calculated for each material class with its mean dynamic properties; the fractiles of the stiffness profiles and of Ts are reported in Chapter 5.1 and are not propagated as additional realizations in the displacement calculation, and each material class is kept as a separate scenario through the inversion to kmax, so the displacement curves are not averaged across materials before that operation.

For each model and realization, the computed Dn(ky) relation is projected onto a non-increasing curve and inverted in the (lnDn,lnky) plane to solve the criterion of 5.13; when Da falls outside the calculated range, the relation is extrapolated in that plane from the two points at the corresponding end, with the single exception of the AM88 limit treated in Appendix 6.5. The inversion is performed first for each model within each realization. The root distributions of the models are then combined with the family weights and summarized through the arithmetic mean and the empirical fractiles q=0.05, 0.10, 0.16, 0.50, 0.84, 0.90, and 0.95 (Verri Kozlowski, 2026a). Because of the decreasing relation between Dn and ky, the fractile associated with the exceedance target satisfies expression 5.15, where q=0.84 corresponds to an exceedance probability of pe=16%.

q=1−pe	(5.15)

The q fractiles are therefore the statistics associated with the criterion expressed through pe; the arithmetic mean summarizes the center of the simulated distribution and does not represent a target probability. The evaluation uses 300 realizations for each demand – the probabilistic spectrum of each return period TR = 100, 200, 500, 1,000, 2,000, 2,500, 5,000, 10,000 years and the MCE – and a grid of allowable displacements Da ranging from 1.35 to 337.50 cm. This grid contains, for every slope height, the damage thresholds Da/H = 0.1, 0.4, 1.0, 2.5% of Chapter 4.2, at which the coefficient tables are reported and which the coefficient figures shade; values of Da that exceed the calculated range of a realization are obtained through the logarithmic extrapolation defined above.

The Newmark displacements were computed with the ensemble set of five formulations: AM88, JB07, and SR08 for the rigid block, and BT07 and BM19 for the flexible block, BM19 being the branch for projects with crustal control, with equal weights. Every formulation received the reference magnitude assigned to each seismic demand and the demand of each of the 8 return periods, 100, 200, 500, 1,000, 2,000, 2,500, 5,000, and 10,000 years, and of the MCE, with 300 realizations per demand, over the 5 slope heights from 27 to 135 m, the 8 material classes, and the relative displacement grid Da/Hs = 0.05, 0.10, 0.25, 0.40, 0.50, 1.00, and 2.50 %.

The reference magnitudes assigned to the seismic demands were Mw = 5.5 for TR = 100, 200, 500, 1,000, 2,000, and 2,500 years; Mw = 6.5 for TR = 5,000 and 10,000 years and the MCE. Within each demand, the same magnitude was used for the geometry–material combinations.

The Newmark displacement curves are developed in the Ground-Motion Design Parameters annex.

The seismic coefficients kmax and kh are developed in the Ground-Motion Design Parameters annex.

Table 5.4: MCE seismic coefficients kh [% of PGA] from the ensemble model. Each cell reports the minimum–maximum range across the material scenarios, from their mean estimates. The range describes variation between materials; it is not a confidence interval or a simulation fractile. siteID identifies the site and Hs the slope height, in m. The remaining column headings are the relative displacement limits Da/Hs [%]. The column colors match the performance bands in the figures.

| siteID | Hs | 0.1% | 0.4% | 1% | 2.5% |
| --- | --- | --- | --- | --- | --- |
| CFD | 27 | 33.6–42.0 | 19.2–23.8 | 11.8–14.7 | 6.4–8.0 |
| CFD | 32 | 31.5–38.9 | 18.2–22.0 | 11.4–13.4 | 6.3–7.4 |
| CFD | 35 | 30.6–38.1 | 17.4–21.2 | 10.6–12.9 | 5.8–6.9 |
| CFD | 50 | 25.7–29.5 | 14.0–16.2 | 8.1–9.6 | 4.2–5.1 |
| CFD | 135 | 16.3–17.5 | 7.7–8.4 | 4.1–4.5 | 2.2–2.4 |

# References

Abrahamson, N. A., & Gulerce, Z. (2022). Summary of the Abrahamson and Gulerce NGA-SUB Ground-Motion Model for Subduction Earthquakes. Earthquake Spectra, 38(2), 1207–1231. https://doi.org/10.1177/87552930221114374

Abrahamson, N. A., Kuehn, N., Gulerce, Z., Gregor, N., Bozorgnia, Y., Parker, G., Stewart, J., Boore, D., Campbell, K., Chiou, B., Idriss, I. M., Youngs, R., & Atkinson, G. (2018). Update of the BC Hydro Subduction Ground-Motion Model using the NGA-Subduction Dataset (No. 2018/02). Pacific Earthquake Engineering Research Center. https://peer.berkeley.edu/publications/2018-02

Abrahamson, N., Gregor, N., & Addo, K. (2016). BC Hydro Ground Motion Prediction Equations for Subduction Earthquakes. Earthquake Spectra, 32(1), 23–44. https://doi.org/10.1193/051712EQS188MR

Aliberti, D., Biondi, G., Cascone, E., & Rampello, S. (2019). Performance Indexes for Seismic Analyses of Earth Dams. In F. Silvestri & N. Moraci (Eds.), Earthquake geotechnical engineering for protection and development of environment and constructions (pp. 1066–1073). Associazione Geotecnica Italiana.

Ambraseys, N. N., & Menu, J. M. (1988). Earthquake-induced Ground Displacements. Earthquake Engineering & Structural Dynamics, 16(7), 985–1006. https://doi.org/10.1002/eqe.4290160704

Anderson, D. G., Martin, G. R., Lam, I. P., & Wang, J. N. (2008). Seismic Analysis and Design of Retaining Walls, Buried Structures, Slopes, and Embankments (NCHRP Report No. 611). Transportation Research Board. https://www.ce.memphis.edu/7137/PDFs/Seismic%20Manual/nchrp_rpt_611.pdf

Aristeidou, S., Shahnazaryan, D., & O’Reilly, G. J. (2024). Ground motion prediction equations using artificial neural networks for active shallow crustal earthquakes. Soil Dynamics and Earthquake Engineering. https://doi.org/10.1016/j.soildyn.2024.108851

Atkinson, G. M. (2022). Backbone Ground Motion Models for Crustal Earthquakes in the 2022 New Zealand National Seismic Hazard Model. Bulletin of the Seismological Society of America, 114(1), 350–370. https://pubs.geoscienceworld.org/ssa/bssa/article-abstract/114/1/350/631700/

Atkinson, G. M., & Boore, D. M. (2006). Earthquake Ground-Motion Prediction Equations for Eastern North America. Bulletin of the Seismological Society of America, 96(6), 2181–2205. https://doi.org/10.1785/0120050245

Atkinson, G. M., & Boore, D. M. (2011). Modifications to Existing Ground-Motion Prediction Equations in Light of New Data. Bulletin of the Seismological Society of America, 101(3), 1121–1135. https://doi.org/10.1785/0120100270

Atkinson, G. M., & Macias, M. (2009). Predicted Ground Motions for Great Interface Earthquakes in the Cascadia Subduction Zone. Bulletin of the Seismological Society of America, 99(3), 1552–1578. https://pubs.geoscienceworld.org/ssa/bssa/article-abstract/99/3/1552/350126

Australian National Committee on Large Dams. (2012). Guidelines on Tailings Dams: Planning, Design, Construction, Operation and Closure. Australian National Committee on Large Dams.

Australian National Committee on Large Dams (ANCOLD). (2019). Guidelines on Tailings Dams – Planning, Design, Construction, Operation and Closure (2019 Update). Addendum to ANCOLD Guidelines on Tailings Dams, July 2019; ANCOLD.

Baker, J. W., Bradley, B. A., & Stafford, P. J. (2021). Seismic Hazard and Risk Analysis. Cambridge University Press. https://doi.org/10.1017/9781108425056

Baker, J. W., & Cornell, C. A. (2006). Spectral Shape, Epsilon and Record Selection. Earthquake Engineering & Structural Dynamics, 35(9), 1077–1095. https://doi.org/10.1002/eqe.571

Baker, J. W., & Jayaram, N. (2008). Correlation of Spectral Acceleration Values from NGA Ground Motion Models. Earthquake Spectra, 24(1), 299–317. https://doi.org/10.1193/1.2857544

Bazzurro, P., & Cornell, C. A. (1999). Disaggregation of Seismic Hazard. Bulletin of the Seismological Society of America, 89(2), 501–520.

Boore, D. M., & Atkinson, G. M. (2008). Ground-motion prediction equations for the average horizontal component of PGA, PGV, and 5%-damped PSA at spectral periods between 0.01 s and 10.0 s. Earthquake Spectra, 24(1), 99–138. https://doi.org/10.1193/1.2830434

Boore, D. M., Stewart, J. P., Skarlatoudis, A. A., Seyhan, E., Margaris, B., Theodoulidis, N., Scordilis, E., Kalogeras, I., Klimis, N., & Melis, N. S. (2021). A Ground-Motion Prediction Model for Shallow Crustal Earthquakes in Greece. Bulletin of the Seismological Society of America, 111(2), 857–874. https://doi.org/10.1785/0120200270

Borcherdt, R. D. (2012). Empirical Evidence for Site Coefficients in Building Code Provisions. Earthquake Spectra, 28(S1), S17–S35. https://doi.org/10.1193/1.4000047

Bradley, B. A. et al. (2022). The Ground Motion Characterization Model for the 2022 New Zealand National Seismic Hazard Model. Bulletin of the Seismological Society of America, 114(1), 329–349. https://pubs.geoscienceworld.org/ssa/bssa/article/114/1/329/631789/

Bray, J. D., & Macedo, J. (2019). Procedure for Estimating Shear-Induced Seismic Slope Displacement for Shallow Crustal Earthquakes. Journal of Geotechnical and Geoenvironmental Engineering, 145(12), 04019106. https://doi.org/10.1061/(ASCE)GT.1943-5606.0002143

Bray, J. D., Macedo, J., & Travasarou, T. (2018). Simplified Procedure for Estimating Seismic Slope Displacements for Subduction Zone Earthquakes. Journal of Geotechnical and Geoenvironmental Engineering, 144(3), 04017124. https://doi.org/10.1061/(ASCE)GT.1943-5606.0001833

Bray, J. D., & Travasarou, T. (2007). Simplified Procedure for Estimating Earthquake-Induced Deviatoric Slope Displacements. Journal of Geotechnical and Geoenvironmental Engineering, 133(4), 381–392. https://doi.org/10.1061/(ASCE)1090-0241(2007)133:4(381)

Bray, J. D., & Travasarou, T. (2009). Pseudostatic Coefficient for Use in Simplified Seismic Slope Stability Evaluation. Journal of Geotechnical and Geoenvironmental Engineering, 135(9), 1336–1340. https://doi.org/10.1061/(ASCE)GT.1943-5606.0000012

Building Seismic Safety Council. (2015). NEHRP Recommended Seismic Provisions for New Buildings and Other Structures (Nos. FEMA P-1050-1). Federal Emergency Management Agency.

Campbell, K. W., & Bozorgnia, Y. (2014). NGA-West2 Ground Motion Model for the Average Horizontal Components of PGA, PGV, and 5% Damped Linear Acceleration Response Spectra. Earthquake Spectra, 30(3), 1087–1115. https://doi.org/10.1193/062913EQS175M

Canadian Dam Association. (2019). Dam Safety Guidelines. Canadian Dam Association.

Canadian Dam Association (CDA). (2021). Technical Bulletin: Application of Dam Safety Guidelines to Mining Dams. CDA Technical Bulletin (first issued 2014, updated 2019; published in English 2021); CDA.

Chao, S.-H., Chiou, B., Hsu, C.-C., & Lin, P.-S. (2020). A Horizontal Ground-Motion Model for Crustal and Subduction Earthquakes in Taiwan. Earthquake Spectra. https://doi.org/10.1177/8755293019891711

Cornell, C. A. (1968). Engineering Seismic Risk Analysis. Bulletin of the Seismological Society of America, 58(5), 1583–1606.

Dakoulas, P., & Gazetas, G. (1985). A Class of Inhomogeneous Shear Models for Seismic Response of Dams and Embankments. International Journal of Soil Dynamics and Earthquake Engineering, 4(4), 166–182. https://doi.org/10.1016/0261-7277(85)90037-3

Dragomiretskiy, K., & Zosso, D. (2014). Variational Mode Decomposition. IEEE Transactions on Signal Processing, 62(3), 531–544. https://doi.org/10.1109/TSP.2013.2288675

European Committee for Standardization. (2004). Eurocode 8: Design of Structures for Earthquake Resistance – Part 5: Foundations, Retaining Structures and Geotechnical Aspects (European Standard Nos. EN 1998-5). European Committee for Standardization.

Federal Emergency Management Agency. (2005). Federal Guidelines for Dam Safety: Earthquake Analyses and Design of Dams (Nos. P-65). Federal Emergency Management Agency.

GEM Foundation. (2023). OpenQuake Engine User Manual. https://docs.openquake.org/oq-engine/current/manual/

Geotechnical Site Investigations, Pub. L. No. AS 1726 (2017).

Global Earthquake Model Foundation. (2024). OpenQuake Engine User Manual, Version 3.21. https://docs.openquake.org/oq-engine/3.21/

Global Tailings Review (ICMM, UNEP, PRI). (2020). Global Industry Standard on Tailings Management. https://globaltailingsreview.org/wp-content/uploads/2020/08/global-industry-standard-on-tailings-management.pdf; Global Tailings Review.

Goulet, C. A., Bozorgnia, Y., Abrahamson, N., et al. (2017). Central and Eastern North-America Ground-Motion Characterization – NGA-East: Final Report (No. 2017/03). Pacific Earthquake Engineering Research Center. https://peer.berkeley.edu/new-peer-report-201703

Hardin, B. O., & Black, W. L. (1968). Vibration Modulus of Normally Consolidated Clay. Journal of the Soil Mechanics and Foundations Division, 94(2), 353–369. https://doi.org/10.1061/JSFEAQ.0001100

Hardin, B. O., & Drnevich, V. P. (1972). Shear Modulus and Damping in Soils: Measurement and Parameter Effects. Journal of the Soil Mechanics and Foundations Division, 98(6), 603–624. https://doi.org/10.1061/JSFEAQ.0001756

Hashash, Y. M. A., Ilhan, O., Harmon, J. A., Parker, G. A., Stewart, J. P., Rathje, E. M., Campbell, K. W., & Silva, W. J. (2020). Nonlinear Site Amplification Model for Ergodic Seismic Hazard Analysis in Central and Eastern North America. Earthquake Spectra, 36(1), 69–86. https://doi.org/10.1177/8755293019878193

Huang, N. E., Shen, Z., Long, S. R., Wu, M. C., Shih, H. H., Zheng, Q., Yen, N.-C., Tung, C. C., & Liu, H. H. (1998). The Empirical Mode Decomposition and the Hilbert Spectrum for Nonlinear and Non-Stationary Time Series Analysis. Proceedings of the Royal Society of London. Series A: Mathematical, Physical and Engineering Sciences, 454(1971), 903–995. https://doi.org/10.1098/rspa.1998.0193

International Commission on Large Dams. (2016). Selecting Seismic Parameters for Large Dams – Guidelines (Bulletin No. 148). International Commission on Large Dams.

Ishihara, K. (1996). Soil Behaviour in Earthquake Geotechnics. Clarendon Press; Oxford University Press. https://doi.org/10.1093/oso/9780198562245.001.0001

Jaimes, M. A., & Garcia-Soto, A. D. (2020). Updated Ground-Motion Prediction Equations for Mexican Intermediate-Depth Intraslab Earthquakes Including V/H Ratios. Earthquake Spectra, 36(1), 196–216. https://doi.org/10.1177/8755293019899947

Jibson, R. W. (2007). Regression Models for Estimating Coseismic Landslide Displacement. Engineering Geology, 91(2–4), 209–218. https://doi.org/10.1016/j.enggeo.2007.01.013

Kotha, S. R., Weatherill, G., Bindi, D., & Cotton, F. (2020). A Regionally-Adaptable Ground-Motion Model for Shallow Crustal Earthquakes in Europe. Bulletin of Earthquake Engineering, 18, 4091–4125. https://doi.org/10.1007/s10518-020-00869-1

Kramer, S. (1997). Geotechnical earthquake engineering. Prentice Hall.

Kuehn, N. M., Bozorgnia, Y., Campbell, K. W., & Gregor, N. (2020). Partially Non-Ergodic Ground-Motion Model for Subduction Regions Using the NGA-Subduction Database (No. 2020/04). Pacific Earthquake Engineering Research Center. https://peer.berkeley.edu/publications/2020-04

Luco, N., Ellingwood, B. R., Hamburger, R. O., Hooper, J. D., Kimball, J. K., & Kircher, C. A. (2007). Risk-targeted versus Current Seismic Design Maps for the Conterminous United States. SEAOC 2007 Convention Proceedings.

Macedo, J., Bray, J. D., Abrahamson, N. A., & Travasarou, T. (2018). Performance-based Probabilistic Seismic Slope Displacement Procedure. Earthquake Spectra, 34(2), 673–695. https://doi.org/10.1193/122516EQS251M

Makdisi, F. I., & Seed, H. B. (1978). Simplified Procedure for Estimating Dam and Embankment Earthquake-Induced Deformations. Journal of the Geotechnical Engineering Division, 104(GT7), 849–867. https://doi.org/10.1061/AJGEB6.0000668

McGuire, R. K. (2004). Seismic Hazard and Risk Analysis. Earthquake Engineering Research Institute.

Minimum Design Loads and Associated Criteria for Buildings and Other Structures, Pub. L. No. ASCE/SEI 7-22 (2022).

Montalva, G. A., Bastias, N., & Rodriguez-Marek, A. (2017). Ground-motion Prediction Equation for the Chilean Subduction Zone. Bulletin of the Seismological Society of America, 107(2), 901–911. https://doi.org/10.1785/0120160221

Motaghed, S., Eftekhari, N., & Mohammadi, M. (2023). Logic tree branch weight assignment and epistemic uncertainty representation in probabilistic seismic hazard analysis. Journal of Seismology. https://doi.org/10.1007/s10950-023-10177-1

National Building Code of Canada, Pub. L. No. NBC 2020 (2020).

NEHRP Consultants Joint Venture. (2011). Selecting and Scaling Earthquake Ground Motions for Performing Response-History Analyses (Nos. NIST GCR 11-917-15). National Institute of Standards; Technology.

Newmark, N. M. (1965). Effects of Earthquakes on Dams and Embankments. Géotechnique, 15(2), 139–160. https://doi.org/10.1680/geot.1965.15.2.139

Parker, G. A., Stewart, J. P., Boore, D. M., Atkinson, G. M., & Hassani, B. (2022). NGA-Subduction Global Ground Motion Models with Regional Adjustment Factors. Earthquake Spectra, 38(2), 456–493. https://doi.org/10.1177/87552930211034889

Pezeshk, S., Zandieh, A., & Tavakoli, B. (2011). Hybrid Empirical Ground-Motion Prediction Equations for Eastern North America Using NGA Models and Updated Seismological Parameters. Bulletin of the Seismological Society of America, 101(4), 1859–1870. https://doi.org/10.1785/0120100082

Phung, V.-L., Abrahamson, N., Mazzoni, S., & Bozorgnia, Y. (2020). Ground Motion Models for Taiwan: Crustal and Subduction Earthquakes. Earthquake Spectra. https://journals.sagepub.com/doi/abs/10.1177/87552930211061168

Saygili, G., & Rathje, E. M. (2008). Empirical Predictive Models for Earthquake-Induced Sliding Displacements of Slopes. Journal of Geotechnical and Geoenvironmental Engineering, 134(6), 790–803.

Seismic Permanent Displacements for Tailings Storage Facilities and Waste Rock Dumps. (n.d.). Graduate thesis, University of British Columbia. https://open.library.ubc.ca/soa/cIRcle/collections/59368/items/1.0314230

Shibata, T., & Soelarno, D. S. (1975). Stress-strain Characteristics of Sands Under Cyclic Loading. Proceedings of the Japan Society of Civil Engineers, 1975(239), 57–65. https://doi.org/10.2208/jscej1969.1975.57

Si, H., Midorikawa, S., & Kishida, T. (2020). NGA-Subduction Ground Motion Model for Japan (No. 2020/06). Pacific Earthquake Engineering Research Center. https://peer.berkeley.edu/publications/2020-06

Somerville, P., Graves, R., Collins, N., Song, S. G., Ni, S., & Cummins, P. (2009). Source and Ground Motion Models for Australian Earthquakes. Proceedings of the Australian Earthquake Engineering Society Conference. https://www.aees.org.au/wp-content/uploads/2013/11/Somerville-et-al.pdf

Stewart, J. P., Parker, G. A., Atkinson, G. M., Boore, D. M., Hashash, Y. M. A., & Silva, W. J. (2020). Ergodic Site Amplification Model for Central and Eastern North America. Earthquake Spectra, 36(1), 42–68. https://doi.org/10.1177/8755293019878185

U.S. Army Corps of Engineers. (1995). Earthquake Design and Evaluation for Civil Works Projects (Engineer Regulation Nos. ER 1110-2-1806). U.S. Army Corps of Engineers. https://www.publications.usace.army.mil/Portals/76/Publications/EngineerRegulations/ER_1110-2-1806.pdf

U.S. Army Corps of Engineers. (2003). Slope Stability (Engineer Manual Nos. EM 1110-2-1902). U.S. Army Corps of Engineers. https://www.publications.usace.army.mil/Portals/76/Publications/EngineerManuals/EM_1110-2-1902.pdf

U.S. Army Corps of Engineers. (2005). Stability of Concrete Structures (Engineer Manual Nos. EM 1110-2-2100). U.S. Army Corps of Engineers. https://www.publications.usace.army.mil/portals/76/publications/engineermanuals/em_1110-2-2100.pdf

U.S. Nuclear Regulatory Commission. (2012). Practical Implementation Guidelines for SSHAC Level 3 and 4 Hazard Studies (Nos. NUREG-2117). U.S. Nuclear Regulatory Commission. https://www.nrc.gov/reading-rm/doc-collections/nuregs/staff/sr2117/

Verri Kozlowski, A. (2023). Modelos Paramétricos para la Selección de Sismos de Diseño en Infraestructura Minera. IV Seminario de Vinculación y Transferencia (SeVyT). https://sevyt23.srk.ar/article.pdf

Verri Kozlowski, A. (2026a). Probabilistic Estimation of Newmark Displacements and Seismic Coefficients under Hazard Uncertainty.

Verri Kozlowski, A. (2026b). Spectral Matching of Recorded Ground Motions Using Variational Mode Decomposition.

Weatherill, G., & Cotton, F. (2020). A Ground Motion Logic Tree for Seismic Hazard Analysis in the Literature of the European Seismic Hazard Model for Stable Craton Regions. Bulletin of Earthquake Engineering, 18, 6119–6148. https://doi.org/10.1007/s10518-020-00940-x

# 6	Appendices

## 6.1	Notation

The following tables summarize the mathematical notation of the report, by thematic block and in order of appearance.

### 6.1.1	General symbols

| Symbol | Definition |
| --- | --- |
| Tn | Oscillator period associated with spectral ordinate n; by convention, Tn=0 represents PGA (s). |
| TR | Return period, TR=1/λI(i*) (yr). |
| VS30 | Travel-time-averaged shear-wave velocity in the uppermost 30 m; it identifies a site condition, not a site class (m/s). |
| Vref | Shear-wave velocity of the reference input condition; 760 and 3000 m/s occur in the formulation (m/s). |

### 6.1.2	Seismic hazard

| Symbol | Definition |
| --- | --- |
| Mw | Moment magnitude. |
| I | Ground-motion intensity measure. |
| i* | Intensity level whose exceedance is evaluated. |
| λI(i*) | Total annual exceedance rate; per source, λI(i*)(s) (1/yr). |
| ν0(s) | Annual rate of occurrence of source s above Mmin (1/yr). |
| Mmin, Mmax(s) | Minimum magnitude of the domain and source upper bound. |
| P1yr, PT | Probability of at least one exceedance in 1 year / in T years. |
| ηI | GMM median intensity in linear units. |
| σlnI | Total logarithmic standard deviation of the GMM. |
| τ, ϕ | Inter-event and intra-event deviations; σlnI2=τ2+ϕ2. |
| ε, ε* | GMM standard-normal residual; number of deviations by which i* exceeds the median. |
| RJB, Rrup, Rx, Rhypo, Repi; z1.0, z2.5, ztor, W, h | Distance metrics and geometric parameters required by the GMMs (km). |
| θk,j,ℓ | Conditional probability that exceedance originates in the magnitude–distance–residual bin (k,j,ℓ); its maximum defines the modal scenario. |

### 6.1.3	DSHA

| Symbol | Definition |
| --- | --- |
| e | Deterministic scenario within the analyzed set E. |
| μrg, σrg | Mean and deviation of lnI for rupture realization r and GMM branch g; with k=(r,g), also written μk, σk. |
| wk=vg/NR | Weight of component k: branch weight over the number of rupture variants; k​wk=1. |
| Sa(84%)(Tn) | 84th-percentile envelope over the scenario set (g). |

### 6.1.4	GMM mixture

| Symbol | Definition |
| --- | --- |
| wk | Weight of GMM branch k in the ensemble; k​wk=1. |
| λI, λI(k) | Mean hazard curve and branch-k curve (1/yr). |
| εij=ηi+δij | Mixed-effects partition of the total residual of record j of event i: inter-event term ηi and intra-event term δij. |

### 6.1.5	Site response

| Symbol | Definition |
| --- | --- |
| Sao(Tn) | Spectral-acceleration random variable obtained from the GMMs in the hazard model; the superscript o does not denote “rock” (g). |
| Sas(Tn,VS30) | Spectral-acceleration random variable obtained by applying ST20 to Sao(Tn) evaluated at the reference condition (g). |
| Sa | Random variable resulting from the mixture of Sao and Sas (g). |
| α | Mixture coefficient assigned to the Sao component; 1−α is assigned to Sas. |
| PGAo | PGA random variable obtained from the GMMs and used as the ST20 input intensity (g). |
| pga* | Realization of PGAo conditioning the ST20 nonlinear term (g). |
| F | Random ST20 amplification factor relating Sas to Sao. |
| Fcomp | Composite amplification model, Fcomp=F760FVFnl; the factor applied from 760 m/s is the ratio between Fcomp at the target and at the reference condition. |
| F760 | Adjustment factor between the 760 m/s condition and the 3000 m/s hard-rock reference. |
| FV | Linear site-amplification factor; it equals one at the 760 m/s reference. |
| Fnl | Nonlinear amplification factor. |
| μlnF, σlnF | Mean and total standard deviation of lnF, conditional on Tn, VS30, and pga*. |
| σL, σI, σNL | Linear, reference-change, and nonlinear contributions to σlnF. |
| AF | Published amplification factor: mean and quantiles of the ratio between the site-condition demand and the reference-rock demand; exactly 1 at VS30=760 m/s. |

### 6.1.6	Seismic record selection

| Symbol | Definition |
| --- | --- |
| CAV | Cumulative absolute velocity of the record. |
| CAV5 | Cumulative absolute velocity restricted to the intervals where the acceleration exceeds 5 cm/s². |
| Sa(Tj), Sat(Tj) | Spectral mean of the scaled record set and target spectrum (g). |

### 6.1.7	MCER

| Symbol | Definition |
| --- | --- |
| Cx | Spectral collapse capacity of the generic fragility anchored at ordinate x: lognormal with P[Cx≤x]=0.10 and σlnC=0.60 (g). |
| λC(x) | Annual collapse rate; λC−1 is its functional inverse (1/yr). |
| Sa(Tn) | Deterministic lower-limit ordinate of Table 21.2-1 (g). |
| SaM(Tn) | Site-specific MCER ordinate (ASCE/SEI 7-22 Section 21.2.3) (g). |
| Sa(Tn) | Design-spectrum ordinate, 23SaM(Tn) (normative symbol, Eq. 21.3-1) (g). |
| SDS, SD1, T* | Section 21.4 design acceleration parameters (g) and period limit (s). |
| SMS=1.5SDS, SM1=1.5SD1 | MCER parameters (g). |
| T0, TS, TL | Corner periods of the Section 11.4.5 code-form spectrum: T0=0.2 SD1/SDS, TS=SD1/SDS; TL is the long-period transition (s). |

### 6.1.8	Slope dynamics

| Symbol | Definition |
| --- | --- |
| Hs, s, λo=b/bmax | Slope height (m), slope ratio, and truncation ratio, with b and bmax the berm and base widths. |
| Go, mo | Fitted basal small-strain shear modulus (MPa) and inhomogeneity factor governing the shear-modulus profile. |
| VSo | Basal shear-wave velocity associated with Go (m/s). |
| Ts | Fundamental period of the slope (Dakoulas–Gazetas) (s). |

### 6.1.9	Displacements and seismic coefficients

| Symbol | Definition |
| --- | --- |
| Dn | Newmark permanent displacement (cm). |
| μlnD, σlnD | Mean and standard deviation of lnDn defined by each displacement model. |
| IA | Arias intensity, derived from PGA through the relation adopted in the report (m/s). |
| Da | Allowable permanent displacement (cm). |
| Da/H | Relative residual displacement (%). |
| ay, ky=ay/g | Yield acceleration (m/s²) and its dimensionless form. |
| r, r⋆ | Ratio ky/PGA and its capped form min(ky/PGA,0.9999) (AM88). |
| kmax(pe∣Da) | Smallest ky whose probability of exceeding Da does not exceed pe (g). |
| pe | Target exceedance probability of the coefficient; the associated empirical fractile is q=1−pe. |
| kh=100 kmax/PGA(VS30) | Seismic coefficient normalized by the site-condition PGA (%). |

## 6.2	Ground Motion Prediction Equations (GMPE)

### 6.2.1	Active Shallow Crust (ASC)

The Active Shallow Crust (ASC) ground-motion logic tree applies to all sources classified as the Active Shallow Crust tectonic region type. The tree comprises eight branches, each assigned equal weight wk=0.12500, with the total weight summing to exactly 1.00000. The uniform weighting reflects the equal epistemic standing afforded to all eight GMPEs; the supporting documentation does not provide explicit per-model selection rationale beyond ASC regime applicability.

The eight branches are documented below, with their assigned weight and calibration context:

AristeidouEtAl2024 (weight: 0.12500). A GMPE for active shallow crustal earthquakes developed using an artificial neural network regression on strong-motion data (Aristeidou et al., 2024). The model is calibrated for the ASC regime with records from events of Mw≥4.5.

Atkinson2022Crust (weight: 0.12500). A backbone crustal GMPE developed by Atkinson (2022) for the 2022 Aotearoa New Zealand National Seismic Hazard Model (NZ22), applying an equivalent point-source framework calibrated against New Zealand strong-motion observations spanning approximately Mw 4.0 to 8.0 at rupture distances up to approximately 400 km (Atkinson, 2022; Bradley et al., 2022). The model is calibrated specifically for the New Zealand crustal (ASC) setting.

BooreEtAl2020 (weight: 0.12500). The GMPE by Boore et al. (2021) for active shallow crustal earthquakes in Greece, published in the Bulletin of the Seismological Society of America, which adapts a global NGA-West2-family model to the faster attenuation and weaker magnitude scaling observed in Greek strong motions.

CampbellBozorgnia2019 (weight: 0.12500). The Campbell-Bozorgnia NGA-West2 model, implemented in OpenQuake via the campbell_bozorgnia_2014.py module and representing a 2019 update to the 2014 NGA-West2 CB model (Campbell & Bozorgnia, 2014). The model is calibrated for active shallow crustal earthquakes using the NGA-West2 database, covering approximately Mw 3.3 to 8.5 at distances up to 300 km.

ChaoEtAl2020Asc (weight: 0.12500). The active shallow crustal variant of a horizontal ground-motion model for Taiwan developed by Chao et al. (2020) (Chao et al., 2020), calibrated from a Taiwan strong-motion flat-file of more than 40,000 recordings spanning 1992 to 2016 using a two-step maximum-likelihood regression procedure. The model is calibrated for the Taiwan crustal regime.

KothaEtAl2020 (weight: 0.12500). The backbone GMPE by Kotha et al. (2020) for active shallow crustal earthquakes in Europe, published in the Bulletin of Earthquake Engineering (Kotha et al., 2020), serving as the ASC component of the 2020 European Seismic Hazard Model (ESHM20). The model was calibrated from the Engineering Strong Motion (ESM) dataset comprising 23,014 recordings from 2,179 earthquakes predominantly in Italy, Turkey, and Greece, spanning Mw 3.0 to 7.4 and Joyner-Boore distances from 0 to approximately 300 km. A hinge magnitude Mh=6.2 separates quadratic from linear magnitude scaling.

PhungEtAl2020Asc (weight: 0.12500). The active shallow crustal variant of a GMPE by Phung et al. (2020) (Phung et al., 2020), calibrated from the Taiwan strong-motion database using 13,415 ground-motion records from 187 crustal events. The model adopts a functional form based on Chiou and Youngs (2014) with Taiwan-specific recalibration and spans approximately Mw 3.5 to 8.0.

Stafford2022 (weight: 0.12500). A backbone crustal GMPE developed by Stafford (2022) for the 2022 New Zealand National Seismic Hazard Model as part of the NZ22 model set (Bradley et al., 2022), derived through adjustments to the Chiou and Youngs (2014) response spectral model. The model is calibrated for the New Zealand ASC setting, spanning Mw 4.5 to 8.4 at rupture distances from 0 to approximately 300 km.

### 6.2.2	Stable Continental Crust (SCC)

The Stable Continental Crust (SCC) ground-motion logic tree applies to all sources classified as the Stable Continental Crust tectonic region type. The tree comprises six branches with a quasi-uniform weighting scheme: five branches each carry a weight of 0.16667 and the sixth (CollapsedNGAEastUSGS) carries the complementary residual weight of 0.16665, ensuring the total sums to exactly 1.00000. The SCC tree does not achieve exact uniform weighting, owing to the rounding required by the six-branch structure. The SCC tree contains fewer branches than the ASC, SIF, and SIS trees, reflecting the more limited number of GMPEs calibrated directly for stable continental regions.

The six branches are documented below, with their assigned weight and calibration context:

Atkinson2008prime (weight: 0.16667). This is OpenQuake’s implementation of the Atkinson referenced empirical relation for Eastern North America with the adjustment published by Atkinson and Boore (2011). The model applies to the stable continental regime.

AtkinsonBoore2006Modified2011 (weight: 0.16667). The Atkinson and Boore (2006) stochastic-based GMPE for Eastern North America (Atkinson & Boore, 2006), subsequently modified in 2011 to incorporate magnitude-dependent stress-drop scaling that improved agreement with newer observational data. The model is calibrated for the stable continental ENA regime.

PezeshkEtAl2011 (weight: 0.16667). A hybrid empirical GMPE for Central and Eastern North America (CENA) by Pezeshk, Zandieh, and Tavakoli (2011), published in the Bulletin of the Seismological Society of America (Pezeshk et al., 2011). The model combines NGA-West1 model predictions with stochastic ground-motion simulations adjusted to ENA source and attenuation parameters, spanning Mw 4.0 to 8.0 at rupture distances up to approximately 1,000 km, reflecting the long-range attenuation characteristics of stable continental crust.

ESHM20Craton (weight: 0.16667). The craton-specific GMPE developed by Weatherill and Cotton (2020) for the 2020 European Seismic Hazard Model (ESHM20), published in the Bulletin of Earthquake Engineering (Weatherill & Cotton, 2020). The model is constructed through a scaled backbone approach adapting Eastern North American GMPEs to characterize epistemic uncertainty in European craton ground motion, designed for stable cratonic environments such as the East European Craton.

SomervilleEtAl2009YilgarnCraton_SS14 (weight: 0.16667). A ground-motion model by Somerville et al. (2009) for rock sites in the Australian Yilgarn Craton, derived from stochastic simulations constrained by regional seismological parameters (Somerville et al., 2009). The model covers source magnitudes in the range Mw 5.0 to 7.5 and captures enhanced long-period ground motion associated with surface waves in this stable cratonic environment. The SS14 designation indicates that the standard deviation model has been updated using the Seyhan and Stewart (2014) formulation.

CollapsedNGAEastUSGS (weight: 0.16665). A custom GSIM registered via the project’s gmm.gmpe extension module, extending the OpenQuake NGAEastUSGSGMPE base class (Goulet et al., 2017). This implementation collapses the ensemble of NGA-East USGS ground-motion models into a single GSIM by pre-computing model predictions into a runtime HDF5 lookup table (NGAEastUSGS_collapsed.hdf5) and inflating the total standard deviation with a stored between-model epistemic term, thereby preserving the spread of the original multi-model suite within a single logic tree branch. The underlying NGA-East USGS models were developed for Central and Eastern North America (CENA) through a SSHAC Level 3 process, covering Mw 4.0 to 8.2 at distances up to approximately 1,500 km. The collapsed implementation requires only VS30 and moment magnitude; distance enters the model internally through the precomputed lookup table.

### 6.2.3	Subduction Interface (SIF)

The Subduction Interface (SIF) ground-motion logic tree applies to all sources classified as the Subduction Interface tectonic region type. The tree comprises ten branches, each assigned equal weight wk=0.10000, with the total weight summing to exactly 1.00000. All ten models are calibrated for subduction interface conditions.

The ten branches are documented below, with their assigned weight and calibration context:

AbrahamsonEtAl2018SInter (weight: 0.10000). An update to the BC Hydro subduction interface GMPE by Abrahamson, Gregor, and Addo, published as PEER Report 2018/02 (N. A. Abrahamson et al., 2018). The original 2016 model was calibrated from 953 recordings of 43 interface events spanning Mw 6.0 to 8.4 at distances up to 300 km, with magnitude scaling constrained by numerical simulations for Mw>8.0 (N. Abrahamson et al., 2016); the 2018 update extended coverage using the NGA-Subduction dataset to approximately Mw 6.0 to 9.0. The model is calibrated for global subduction interface conditions.

AbrahamsonGulerce2020SInter (weight: 0.10000). The subduction interface component of the NGA-Subduction regionalized GMPE by Abrahamson and Gulerce (2022), developed under the PEER NGA-Sub program (N. A. Abrahamson & Gulerce, 2022). The model was calibrated from 3,914 recordings of 113 interface events spanning Mw 5.0 to 9.2 from the NGA-SUB global database, with region-specific adjustments for seven subduction zones including Cascadia, Japan, New Zealand, South America, Central America and Mexico, Alaska, and Taiwan.

Atkinson2022SInter (weight: 0.10000). The subduction interface backbone GMPE developed by Atkinson (2022) for the 2022 New Zealand National Seismic Hazard Model (NZ22), applying an equivalent point-source framework adapted to interface earthquake kinematics (Atkinson, 2022). The model is calibrated for the New Zealand subduction interface setting, with empirical constraints spanning approximately Mw 4.0 to 7.0 at distances up to approximately 400 km.

AtkinsonMacias2009NSHMP2014 (weight: 0.10000). The subduction interface GMPE by Atkinson and Macias (2009) as implemented for the 2014 National Seismic Hazard Mapping Program (Atkinson & Macias, 2009), originally developed for the Cascadia subduction zone using stochastic simulations anchored to recordings from the 2003 Tokachi-Oki earthquake sequence in Japan with subsequent adjustments for Cascadia source and attenuation conditions. The model targets large interface events in the magnitude range Mw 7.5 to 9.0.

ChaoEtAl2020SInter (weight: 0.10000). The subduction interface variant of the Taiwan ground-motion model by Chao et al. (2020) (Chao et al., 2020), calibrated from the Taiwan strong-motion flat-file for interface earthquake records.

KuehnEtAl2020SInter (weight: 0.10000). The subduction interface component of a partially non-ergodic NGA-Subduction GMPE by Kuehn et al. (2020), published as PEER Report 2020/04 (Kuehn et al., 2020). The model was developed through Bayesian regression with informative priors over a NGA-Sub database comprising more than 210,000 ground-motion components from 1,570 events spanning Mw 4.0 to 9.1, providing region-specific constants and attenuation parameters for seven global subduction zones.

MontalvaEtAl2017SInter (weight: 0.10000). The subduction interface GMPE by Montalva et al. (2017), published in the Bulletin of the Seismological Society of America (Montalva et al., 2017), calibrated from 3,774 recordings of 473 earthquakes recorded in Chile between 1985 and 2015, covering Mw 4.6 to 8.8 and Rrup from approximately 20 to 650 km. The model is calibrated for the Chilean subduction interface regime.

ParkerEtAl2020SInter (weight: 0.10000). The subduction interface component of a global NGA-Subduction GMPE by Parker et al. (2022), published as PEER Report 2020/03 and subsequently in Earthquake Spectra (Parker et al., 2022). The model was calibrated from records spanning subduction zones in Japan, Taiwan, New Zealand, Mexico, Central America, South America, Alaska, and Cascadia, covering Mw 4.7 to 9.1 and Rrup from approximately 25 to 2,000 km. The model provides predictions for PGA, PGV, and 5%-damped pseudo-spectral acceleration at 26 oscillator periods from 0.01 to 10 s.

PhungEtAl2020SInter (weight: 0.10000). The subduction interface variant of the GMPE by Phung et al. (2020) (Phung et al., 2020), calibrated from the Taiwan subduction database for interface events spanning approximately Mw 4.0 to 7.6 at distances up to approximately 200 km.

SiEtAl2020SInter (weight: 0.10000). The subduction interface component of a NGA-Subduction regional GMPE by Si et al. (2020), published as PEER Report 2020/06 and developed for Japanese subduction earthquakes (Si et al., 2020).

### 6.2.4	Subduction Intraslab (SIS)

The Intermediate-Depth Subduction Intraslab (SIS) ground-motion logic tree applies to all sources classified as the Intermediate-Depth Subduction Intraslab tectonic region type. The tree comprises nine branches of practically equal weight, wk=0.11111 —the first, AbrahamsonEtAl2018SSlab, carries 0.11112 so that the total sums to exactly 1.00000—. The SIS ensemble largely parallels the SIF ensemble in model selection, with the substitution of intraslab-specific GSIM variants (SSlab suffix models in place of SInter variants) and the addition of JaimesEtAl2020SSlab.

The nine branches are documented below, with their assigned weight and calibration context:

AbrahamsonEtAl2018SSlab (weight: 0.11112). The intraslab variant of the BC Hydro subduction GMPE by Abrahamson, Gregor, and Addo (2016) (N. Abrahamson et al., 2016), calibrated for global subduction intraslab conditions from 2,590 recordings of 63 slab events spanning Mw 5.0 to 7.9 at distances up to 300 km.

AbrahamsonGulerce2020SSlab (weight: 0.11111). The intraslab component of the NGA-Subduction regionalized GMPE by Abrahamson and Gulerce (2022) (N. A. Abrahamson & Gulerce, 2022), calibrated from 4,850 recordings of 89 intraslab events spanning Mw 5.0 to 7.8 from the NGA-SUB global database, with region-specific adjustments for seven subduction zones.

Atkinson2022SSlab (weight: 0.11111). The intraslab backbone GMPE developed by Atkinson (2022) for the NZ22 model set (Atkinson, 2022), applying an equivalent point-source framework adapted to intraslab earthquake kinematics. Unlike the interface variant, this implementation requires a backarc classification flag in addition to Rrup, VS30, and moment magnitude, distinguishing forearc and backarc site attenuation conditions. The backarc parameter accounts for the systematically reduced ground-motion amplitudes observed at backarc sites in subduction environments.

ChaoEtAl2020SSlab (weight: 0.11111). The intraslab variant of the Taiwan ground-motion model by Chao et al. (2020) (Chao et al., 2020), calibrated from Taiwan intraslab records.

JaimesEtAl2020SSlab (weight: 0.11111). An updated GMPE for Mexican intermediate-depth intraslab earthquakes by Jaimes and Garcia-Soto (2020), published in Earthquake Spectra (Jaimes & Garcia-Soto, 2020). The model was calibrated from 366 accelerogram records of 23 intraslab events on the Cocos plate subduction system, extended to include recordings from the September 2017 intraslab events in Mexico (including the Mw 8.1 Chiapas normal-faulting event), covering Mw approximately 5.0 to 8.2, Rrup up to approximately 400 km, and focal depths up to approximately 75 km.

KuehnEtAl2020SSlab (weight: 0.11111). The intraslab component of the partially non-ergodic NGA-Subduction GMPE by Kuehn et al. (2020) (Kuehn et al., 2020), using the same Bayesian regression framework as the interface variant but calibrated on intraslab records from the NGA-Sub database.

MontalvaEtAl2017SSlab (weight: 0.11111). The intraslab variant of the Chilean subduction GMPE by Montalva et al. (2017) (Montalva et al., 2017). In contrast to the interface variant, which uses Rrup as the primary distance metric, the intraslab implementation uses Rhypo, consistent with the deeper and more diffuse rupture geometry of intraslab events.

ParkerEtAl2020SSlab (weight: 0.11111). The intraslab component of the global NGA-Subduction GMPE by Parker et al. (2022) (Parker et al., 2022), calibrated for intraslab events spanning Mw 4.0 to 8.4 at Rrup from approximately 35 to 2,000 km.

PhungEtAl2020SSlab (weight: 0.11111). The intraslab variant of the GMPE by Phung et al. (2020) (Phung et al., 2020), calibrated from Taiwan intraslab records.

## 6.3	Normative Seismic Criteria for Tailings Storage Facilities

Table 6.1: GISTM Seismic Design Criteria by Consequence Class. Source: GISTM (2020). The Global Industry Standard on Tailings Management (GISTM) defines five consequence classes for tailings storage facilities, based on population at risk (PAR) and the severity of environmental and socio-economic impacts. For all classes, the maximum credible earthquake (MCE) governs if it produces more severe ground motions than the probabilistic criterion. Post-closure criteria are uniform across all classes. GISTM does not use OBE/SEE terminology or dual-level design earthquakes.

| Class | PAR* | Consequences | Operations and Active-Care Closure† | Passive-Care Post-Closure‡ |
| --- | --- | --- | --- | --- |
| Low | None | No expected loss of life; minimal off‑site impacts. | 1/200 | 1/10,000 |
| Significant | 1–10 | Minor but reportable off‑site impacts. | 1/1,000 | 1/10,000 |
| High | 10–100 | Major localized impacts, potential for multiple fatalities. | 1/2,475 | 1/10,000 |
| Very High | 100–1,000 | Substantial regional impacts, likely multiple fatalities. | 1/5,000 | 1/10,000 |
| Extreme | >1,000 | Catastrophic, long‑term, widespread impacts, >100 likely fatalities. | 1/10,000 | 1/10,000 |
| *PAR = Population at Risk (off‑site persons) |  |  |  |  |
| †Annual-exceedance criteria during operations and active closure. The Extreme 1/10,000 UHS and MCE define the reported design bounds. |  |  |  |  |
| ‡The 1/10,000 UHS and MCE define the reported passive-closure design bounds. |  |  |  |  |

Table 6.2: CDA Seismic Design Criteria by Consequence Classification. Source: CDA Technical Bulletin, Application of Dam Safety Guidelines to Mining Dams (2021), Table 3-3 (construction, operation and transition) and Table 4-2 (closure, passive care). The Canadian Dam Association (CDA) defines five consequence classifications, assigned from population at risk, loss of life, and environmental, cultural and economic losses. The tabulated levels are target levels for initial consideration and consultation between owner and regulator, not fixed requirements: the designer of record and the owner may adopt more stringent levels to further reduce risk, or less stringent ones where justified. The maximum credible earthquake (MCE) is a declared alternative to the probabilistic level, not an upper bound; CDA notes only that the MCE has no associated annual exceedance probability. Passive care is not abandonment: CDA requires a steady-state condition, demonstrated by accumulated experience and monitoring, before a facility enters that phase. CDA does not use OBE/SEE terminology; it specifies an Earthquake Design Ground Motion (EDGM).

| Class | Population at risk | Loss of life* | Construction, Operation and Transition† | Closure and Passive Care‡ |
| --- | --- | --- | --- | --- |
| Low | None | 0 | 1/100 | 1/1,000 |
| Significant | Temporary only | Unspecified | Between 1/100 and 1/1,000 | 1/2,475 |
| High | Permanent | 10 or fewer | 1/2,475 | 1/2 between 1/2,475 and 1/10,000, or MCE |
| Very High | Permanent | 100 or fewer | 1/2 between 1/2,475 and 1/10,000, or MCE | 1/10,000, or MCE |
| Extreme | Permanent | More than 100 | 1/10,000, or MCE | 1/10,000, or MCE |
| *CDA Technical Bulletin Table 3-1, after Table 2-1 of the CDA Dam Safety Guidelines. |  |  |  |  |
| †Annual exceedance probability for earthquakes, CDA Technical Bulletin Table 3-3. The 1/2,475 level is anchored to the National Building Code of Canada. |  |  |  |  |
| ‡Annual exceedance probability for earthquakes, CDA Technical Bulletin Table 4-2. Closure under active care with regular monitoring retains the Table 3-3 levels. |  |  |  |  |

Table 6.3: ANCOLD Seismic Design Criteria by Consequence Category. Source: ANCOLD Guidelines on Tailings Dams (2019). ANCOLD defines six consequence categories based on population at risk (PAR) and expected loss of life, with three gradations for the High category: High C, High B, and High A. OBE and SEE are assigned by consequence category; for post-closure, the SEE of the applicable category is adopted and is reassessed at closure upon changes in the hazard, the condition of the dam, or its consequences. For the Extreme category, the greater of the MCE and the 1/10,000 AEP event governs, evaluated at the 84th percentile. PAR = population at risk.

| Class | PAR | Consequences | OBE | SEE |
| --- | --- | --- | --- | --- |
| Low | 0 | No expected loss of life; negligible off‑site impact. | 1/475 | 1/1,000 |
| Significant | 1–10 | Few persons at risk; minor off‑site or environmental impact. | 1/475 | 1/1,000 |
| High C | 11–100 | Possible loss of life; moderate environmental/economic impact. | 1/475–1/1,000 | 1/2,000 |
| High B | 101–1,000 | Likely multiple fatalities; major environmental/economic loss. | 1/475–1/1,000 | 1/5,000 |
| High A | >1,000 (up to a few thousand) | Likely multiple fatalities; regional/catastrophic impact. | 1/475–1/1,000 | 1/10,000 |
| Extreme | > several thousand | Very high loss of life expected; catastrophic, long‑term impacts. | 1/475–1/1,000 | Greater of MCE or 1/10,000 (85th percentile) |

## 6.4	Site Classification and Ground Properties

### 6.4.1	Site Classification

The seismic site condition is initially characterized by VS30, the time-averaged shear-wave velocity of the uppermost 30 m of the profile. The VS profile is obtained through geophysical investigations appropriate to the project conditions, among them borehole logging, seismic cone penetration tests, and surface-wave methods. The definition of VS30 preserves the shear-wave travel time through the layered profile:

VS30=30i=1NHiVS,i,	(6.1)

where Hi and VS,i are, respectively, the thickness in meters and the shear-wave velocity of layer i within the uppermost 30 m, and N is the number of layers of the profile within that thickness. The expression corresponds to a travel-time average and provides the uniform velocity that reproduces the propagation time of the actual profile. VS30 is the site-condition predictor used by the ground-motion models and by the amplification relations of this assessment (Borcherdt, 2012). It also identifies the reference condition from which the hazard spectra and the rock-to-site transformations are interpreted. In the site-specific analyses, the calculation additionally uses the properties required by the response model; the initial classification does not replace that characterization. The parameter summarizes the average shallow stiffness, but it does not by itself describe stratigraphic contrasts, depth to bedrock, basin effects, or resonance periods. These limitations are considered when defining the scope of a site-specific evaluation and when interpreting the resulting spectral demand.

The NEHRP provisions classify sites into Classes A through E and reserve Class F for conditions requiring site-specific evaluation (Building Seismic Safety Council, 2015). The reference ranges based on VS30 are the following:

Class A: hard rock, with VS30>1500 m/s.

Class B: rock, with VS30 between 760 and 1500 m/s.

Class C: very dense soil or soft rock, with VS30 between 360 and 760 m/s.

Class D: stiff soil, with VS30 between 180 and 360 m/s.

Class E: soft soil, with VS30<180 m/s.

Class F: profiles requiring site-specific evaluation, among them soils susceptible to liquefaction or collapse, peats, organic clays, thick high-plasticity clays, and very soft clays.

Where velocity measurements are available, VS30 is the primary criterion. The provisions also include criteria based on penetration resistance and on undrained shear strength where the geophysical information is insufficient. Class F is not assigned through a single VS30 range and leads to a site response analysis in lieu of the direct application of generic factors.

ASCE/SEI 7-22 updates the discretization of site conditions and distinguishes Classes A, B, BC, C, CD, D, DE, and E through velocity ranges, from competent rock to soft soils (Minimum Design Loads and Associated Criteria for Buildings and Other Structures, 2022). Class F identifies conditions that require site-specific response procedures and is not assigned solely through a VS30 range. The ranges and descriptions of the adopted classification are presented below. The evaluated VS30 values represent the site conditions for which the demand is determined. The class of a particular location is assigned from the applicable geotechnical profile and from the additional conditions defined by the standard.

The evaluated site conditions extend down to VS30=180 m/s, which falls within Class DE; the assessment does not reach Class E. Softer conditions are reserved for site-specific response procedures: Class F requires them under ASCE/SEI 7-22 (Minimum Design Loads and Associated Criteria for Buildings and Other Structures, 2022, Sections 11.4.7, 21.1), and Class E may additionally be assigned through the soft-clay criterion of Section 20.2.2, independently of VS30. The ergodic amplification model declares its applicability for VS30 between 200 and 3000 m/s, and its authors recommend a site-specific response analysis for conditions with VS30 below 200 m/s (Hashash et al., 2020; Stewart et al., 2020). For profiles softer than those evaluated, the spectra and parameters of this report are not applicable without a site-specific response evaluation.

Table 6.4: Seismic site classification. Source: ASCE/SEI 7-22 (Minimum Design Loads and Associated Criteria for Buildings and Other Structures, 2022).

| SC | Description | Vs30 |
| --- | --- | --- |
| A | Hard rock | >1500 [m/s] |
| B | Medium hard rock | >910-1500 [m/s] |
| BC | Soft rock | >640-910 [m/s] |
| C | Very dense soil or hard clay | >440-640 [m/s] |
| CD | Dense sand or very stiff clay | >300-440 [m/s] |
| D | Medium dense sand or stiff clay | >210-300 [m/s] |
| DE | Loose sand or medium stiff clay | >150-210 [m/s] |
| E | Very loose sand or soft clay | <=150 [m/s] |
| F | Soils requiring site response analysis (ASCE/SEI 7-22 21.1) | *See ASCE 7 section 20.2.1 |

The Australian Standard AS 1726-2017 (Geotechnical Site Investigations, 2017) provides guidelines for conducting geotechnical investigations and includes a site classification system that categorises sites into classes based on their soil properties, such as shear wave velocity parameter vS, depth to bedrock, and soil type. The Australian Standard AS 1170.4 “Earthquake Actions on Structures” uses a similar site classification system based on the stiffness of the ground, but it does not explicitly use the shear wave velocity parameter vS to classify the ground. The categories range from A (rock) to E (soft soil), with a special category (S) for sites requiring site-specific investigations.

Table 6.5: Site Classification. Source: Australian Standard AS-1726

| SC | Description | Vs30 |
| --- | --- | --- |
| A | Strong Rocks | >1500 [m/s] |
| B | Rocks | >360 [m/s] |
| C | Shallow soil site | >150 [m/s] |
| D | Deep or soft soil site | >150 [m/s] |
| E | Very soft soil site | <=150 [m/s] |

The National Building Code of Canada (National Building Code of Canada, 2020) provides guidelines for site characterization and seismic site response. Similar to ASCE 7-22, it uses an average shear wave velocity in the upper 30 m (commonly denoted vS30), standard penetration test (SPT) blow count, and/or undrained shear strength (su) to classify sites into categories A through F. Where site-specific investigations are warranted (e.g., liquefiable soils, highly sensitive clays, peat), the code requires more detailed analysis.

Table 6.6: Site Classification. Source: National Building Code of Canada NBC (2020)

| SC | Description | Vs30 |
| --- | --- | --- |
| A | Hard rocks | >1500 [m/s] |
| B | Rocks | >760-1500 [m/s] |
| C | Very dense soils or soft rocks | >360-760 [m/s] |
| D | Stiff soils | >180-360 [m/s] |
| E | Soft soils | >140-360 [m/s] |
| F | Other soils | <=140 [m/s] |

## 6.5	Newmark Permanent-Displacement Formulations

The seismic-coefficient chapter applies five Newmark permanent-displacement formulations: three rigid-block models, two flexible-block models and, among the latter, the BM branch selected by the tectonic control of the project. This appendix reproduces the published form of each formulation, including both BM branches, and states the rule that defines the active configuration. The rigid-block formulations relate the displacement to measures of the base excitation, whereas the flexible-block formulations additionally incorporate the dynamic response of the sliding mass through its fundamental period Ts and the spectral acceleration evaluated at a period proportional to Ts.

## 6.6	Rigid-Block Models

The AM88 formulation (Ambraseys & Menu, 1988) uses the ratio of yield acceleration to PGA, capped to preserve the logarithmic domain, r⋆=min(ky/PGA,0.9999):

μlnD&=ln(10)0.90+log10​(1−r⋆)2.53(r⋆)−1.09,σlnD&=0.30ln(10).	(6.2)

The two remaining rigid-block formulations, JB07 and SR08, use the Arias intensity, which is estimated for each realization from the PGA (Verri Kozlowski, 2023):

IA=exp(2.6109) PGA1.9228.	(6.3)

where IA is expressed in m/s and PGA in units of g; the relation is applied deterministically, so that each PGA realization determines a single value of IA and the displacement sample propagates the PGA variability. The JB07 formulation (Jibson, 2007) incorporates the Arias intensity and the ratio ky/PGA:

μlnD&=ln(10)0.561log10IA−3.833log10​kyPGA−1.474,σlnD&=0.616ln(10).	(6.4)

The SR08 formulation (Saygili & Rathje, 2008) defines r=ky/PGA and combines PGA and Arias intensity:

μlnD=​&2.39−5.24r−18.78r2+42.01r3−29.15r4&−1.56lnPGA+1.38lnIA,σlnD=​&0.46+0.56r.	(6.5)

The logarithmic extension of the Dn(ky) relations beyond their computed support has one exception, the AM88 limit. If the sampled PGA of a realization, PGAs, is smaller than the lower end of the grid, all stored points may satisfy ky/PGAs≥rmax=0.9999 and form a plateau D0,s. In that case the physical branch 0<r<rmax of eq. 6.2 is solved for Da>D0,s, instead of extrapolating the plateau or assigning kmax=0:

μlnD(r)=lnDa−lnD0,s+μlnD(rmax),  kmax,s=PGAsr.	(6.6)

The random residual cancels between Da and D0,s, and dμlnD/dr=−2.53/(1−r)−1.09/r<0, so the root is unique. An AM88 plateau is accepted only when the original curve is exactly constant and PGAs itself shows that the entire grid reached that limit; a flat curve from another model, or a target Da≤D0,s, is rejected as non-identifiable support.

## 6.7	Flexible-Block Models

The flexible-block formulations evaluate the spectral acceleration at a period proportional to the fundamental period Ts of the sliding mass. The BT07 formulation (Bray & Travasarou, 2007) employs Sa=Sa(1.5Ts) and Mw:

μlnD=​&a0−2.83lnky−0.333(lnky)2+0.566lnkylnSa&+3.04lnSa−0.244(lnSa)2+1.50Ts+0.278(Mw−7),a0=​&−0.22,Ts<0.05 s,−1.10,Ts≥0.05 s,σlnD=​&0.66.	(6.7)

The BM17 formulation (Bray et al., 2018) represents subduction-interface motions with Sa=Sa(1.5Ts):

μlnD&=a0+a1lnSa−0.225(lnSa)2,a1&=3.060+0.538lnky,a0,<=​&−5.864+0.550Mw−9.421Ts&−3.353lnky−0.390(lnky)2,a0,≥=​&−6.896+0.550Mw+3.081Ts−0.803Ts2&−3.353lnky−0.390(lnky)2,a0&=a0,<,Ts<0.1 s,a0,≥,Ts≥0.1 s,σlnD&=0.73.	(6.8)

The BM19 formulation (Bray & Macedo, 2019) represents ordinary shallow crustal motions with Sa=Sa(1.3Ts):

μlnD&=a0+2.649+0.344lnkylnSa−0.090(lnSa)2,a0,<=​&−4.684+0.603Mw−9.471Ts&−2.482lnky−0.244(lnky)2,a0,≥=​&−5.981+0.603Mw+3.223Ts−0.945Ts2&−2.482lnky−0.244(lnky)2,a0&=a0,<,Ts<0.1 s,a0,≥,Ts≥0.1 s,σlnD&=0.72.	(6.9)

## 6.8	Ensemble

The active configuration applies five formulations: AM88, JB07, SR08, BT07, and one BM branch – BM17 when the project declares subduction control, BM19 when it declares crustal control; each evaluation therefore applies five formulations, never both BM branches at once. The predictors and dispersions are applied in the published form of each model, and the five formulations are combined with the equal weights and the rigid and flexible families defined in Chapter 5.2.

ε is a random variable representing the residual (in log units) for an individual event

The site-specific procedure of ASCE/SEI 7-22 encompasses the complete determination of the ground motions through site-specific analyses: the probabilistic component of Section 21.2.1, the deterministic component of Section 21.2.2 and, where applicable, the site-response analysis of Section 21.1, as opposed to the general procedure of Section 11.4.6.

The numerical support of ky corresponds to the interval defined in Chapter 5.2; when a complete AM88 realization reaches the limit r⋆=0.9999, its inversion retains the sampled PGA and recovers the physical branch according to eq. 6.6.